An Online Loop Closing Current Calculation Method for Complex Distribution Networks Considering Source and Load Uncertainties

Weifeng Peng1, Licheng Sha2, Kaiyuan Zheng3, Shufeng Dong1*, Xin Zhang1, Jing Tian4

1 College of Electrical Engineering, Zhejiang University  Hangzhou  310027  China

2 State Grid Beijing Electric Power Company  Beijing  100031  China

3 State Grid Beijing Electric Power Company Electric Power Research Institute  Beijing  100075  China

4 State Grid Beijing Electric Power Company Overhaul Branch  Beijing  100073  China

*dongshufeng@zju.edu.cn

Abstract: To address the challenges posed by frequent source and load fluctuations in existing loop closing current calculation methods, this paper proposes an online loop closing current calculation method that considers source and load uncertainties. First, a dual-stack dynamic monitoring system is utilized to obtain real-time voltage and current variations before and after disturbances. Second, Thevenin’s theorem is employed to build an equivalent model of the distribution network, simplifying the complex network into a combination of an independent voltage source and a series impedance. Then, the steady-state loop closing current is calculated based on the open-circuit voltage and equivalent impedance at both sides of the loop closing point. Next, the optimal frequency method is applied to determine the equivalent impedance and attenuation time constant at a specific frequency, achieving accurate calculation of the transient loop closing current. Finally, simulations are conducted to model the fluctuations in distributed generation and load, analyzing the steady-state and transient loop closing currents. The simulation results demonstrate that the proposed method accurately captures the effects of source and load fluctuations on the loop closing current in dynamic environments, with minimal calculation error, indicating its high practicality.

keywords：Loop closing current calculation, source and load uncertainty, dynamic monitoring, Thevenin’s theorem, optimal frequency

1.  Introduction

Loop closing operation is a crucial aspect of power grid management, essential for ensuring the safety and stability of the grid [1]. During loop closing, differences in voltage and impedance across various regions can induce current fluctuations [2, 3]. If the actual current exceeds the safety threshold but is not accurately reflected in the calculations, it may lead to erroneous loop closing operations, resulting in equipment overload or relay protection malfunctions, which could severely compromise the reliability and stability of the distribution network [4]. Therefore, accurately calculating the loop closing current has become a critical challenge in the operation of complex distribution networks.

At present, the calculation of loop closing current primarily relies on topological analysis and equivalent modeling of power systems [5]. Existing modeling methods include both offline and online calculations. Offline calculations mainly use static equivalence methods, which provide relatively accurate results based on known information and are suitable for grid planning and static analysis, such as the Ward equivalent [6], radial equivalent [7], and Thevenin equivalent [8]. However, with the high penetration of distributed generation, offline methods struggle to respond in real-time to source and load fluctuations, thus affecting the accuracy of loop closing current calculations [9, 10].

To overcome the limitations of offline calculations, online calculation methods have become a research focus, typically divided into detailed and simplified modeling approaches [11, 12]. Detailed modeling methods provide high computational accuracy by precisely simulating the topology and dynamic behavior of the power grid. In [13], a depth-first search algorithm based on directed graphs was used to obtain the loop topology, followed by detailed modeling of each node. References [14-16] proposed a series of general modeling methods and improvements tailored for active distribution networks. However, as the system scale expands, the computational complexity of detailed modeling in multi-node, complex scenarios increases significantly, with the computation load growing exponentially. This not only prolongs the iterative process but may also lead to non-convergence.

In contrast, simplified modeling methods enhance computational efficiency by simplifying the topological structure and equivalent processing. Reference [17] employed a third harmonic injection method to estimate grid impedance, but the introduction of external disturbances led to voltage and current distortions, affecting the accuracy of impedance calculation. Reference [18] utilized the extended Kalman filter to estimate the equivalent impedance of the grid in real time, but it relied on large-scale state-space models and Jacobian matrices, which increased computational complexity. Reference [19] compared detailed power flow analysis, simplified power flow analysis, and approximate formula methods, noting that while detailed power flow analysis offers higher accuracy, its computational process is more complex. Simplified and approximate formula methods, on the other hand, significantly reduce computational load, and although there is a slight decrease in accuracy, they remain applicable to most practical scenarios without requiring complex iterative processes. Compared to detailed modeling methods, simplified methods not only improve computational speed but also allow for rapid response to system changes, making them suitable for scenarios with frequent dynamic variations.

The analysis of loop closing current primarily involves the calculation of steady-state and transient currents. Steady-state current reflects the system’s operating characteristics after the loop closing process has reached equilibrium, typically relying on the equivalent model of the system. Transient current, on the other hand, is a short-term peak current caused by voltage differences at the moment of loop closing, which involves complex transient processes [20]. Reference [21] utilized the Newton-Raphson method for detailed modeling of the power grid, iteratively solving for power flow and voltage to obtain the steady-state loop closing current. Reference [22] analyzed the impact of different types of inverters and control strategies on the loop closing current and proposed a transient expression of the current, though no specific numerical calculations were performed. Reference [23] calculated transient currents through a multi-exponential decay transient current equation, but the complexity of the solution increased significantly with the grid’s complexity. Reference [24] derived the formula for calculating the maximum value of transient loop closing current, but did not provide detailed analysis of parameters such as the attenuation time constant.

To address the limitations of existing studies, this paper proposes an online loop closing current calculation method that considers source and load uncertainties. The method introduces a dual-stack structure to monitor real-time voltage and current variations in the grid, capturing the source and load disturbance processes. Based on Thevenin’s theorem, the complex distribution network is simplified into a series representation of open-circuit voltage and equivalent impedance, enabling accurate calculation of both steady-state and transient currents. The main contributions of this paper are as follows:

- The dual-stack structure enables real-time monitoring of voltage and current changes before and after disturbances, providing robust data support for constructing the equivalent model and accurately calculating the loop closing current during system dynamic fluctuations.

- Using system disturbances and Thevenin’s theorem, the proposed method simplifies the modeling of complex branches and distributed generation without introducing external disturbances. This approach significantly reduces modeling and computational complexity, improving efficiency, and making it suitable for large-scale applications in complex distribution networks.

- By combining steady-state current calculations with the optimal frequency method, the proposed method comprehensively analyzes the current behavior during the loop closing process. In addition to steady-state current calculation, the optimal frequency method is used to evaluate transient loop closing current, enabling a complete assessment of both steady-state and transient currents.

The structure of this paper is as follows: Section II briefly analyzes the impact of source and load uncertainty on loop closing current calculation; Section III details the online construction method of the equivalent model for distribution networks; Section IV presents the calculation method for steady-state and transient loop closing currents; Section V validates the proposed method through simulation analysis; finally, Section VI concludes the paper.

2.  Analysis of typical loop closing scenarios and source-load uncertainty

A typical loop closing scenario in a distribution network is illustrated in Figure 1. Before executing the loop closing operation, there is usually a voltage difference between the two sides of the loop closing point due to the network structure and operating conditions. When the loop closing operation is performed, this voltage difference rapidly drops to zero, generating an instantaneous current at the loop closing switch. The magnitude and attenuation characteristics of this current are influenced by system electrical parameters and the distribution of distributed generation and loads.

Based on the upstream network topology and operating conditions, loop closing scenarios can be classified into the following two types:

- Same feeder or same transformer line (e.g., loop closing point between B1 and B3 in Figure 1). The voltage difference at the loop closing point is mainly affected by the feeder impedance and distributed generation and load, typically resulting in a smaller voltage difference;

- Different substation lines (e.g., loop closing point between B2 and B4 in Figure 1). The loop closing point is located between different substations, and the operating conditions of the upstream grid differ, leading to a larger voltage difference at the loop closing point.

FIGURE 1  Schematic diagram of a typical distribution network loop closure scenario

The uncertainty of distributed generation and loads plays a crucial role in the formation of loop closing currents, primarily influencing the following aspects:

- In high-renewable-energy scenarios, the volatility of distributed generation directly affects the magnitude and dynamic characteristics of the loop closing current;

- In high-load-density scenarios, such as urban distribution networks, the load impedance's shunting effect during loop closing becomes more pronounced;

- The location and number of distributed generation and load connections alter the impedance distribution and power characteristics of the distribution network. Particularly when the connection points are close to the loop closing point, they have a direct impact on the loop closing current.

Therefore, when establishing a loop closing current analysis model, it is essential to fully account for the dynamic changes in distributed generation and loads to ensure accurate calculation of loop closing currents under various operating conditions.

3.  Dynamic Monitoring and Equivalent Model Construction for Distribution Networks

3.1.  Dynamic monitoring module based on dual-stack structure

To meet the dynamic computational demands during source and load fluctuations, a dynamic monitoring module based on a dual-stack structure can be employed, as illustrated in Figure 2. The dual-stack structure consists of a recent data stack (S2) and a historical data stack (S1), which store electrical parameters from the current and historical moments of the system, respectively. Each stack contains n data points used to record the corresponding voltage and current parameters along with timestamps, where n is determined by the granularity required to capture the disturbance process. To prevent excessive data accumulation and avoid unnecessary consumption of computational resources, the system manages the data using a "new data in, old data out" mechanism. This ensures efficient and reasonable utilization of computational resources.

FIGURE 2  Mechanism diagram of dynamic monitoring with data stack capture

When the system detects a significant change in the voltage or current data in S2n, it indicates that the system has been disturbed, triggering the capture mechanism. Both stacks will then simultaneously record and update the data changes during the disturbance process until S1n detects the disturbance point, marking the end of the disturbance capture process. After capture is completed, the data points S1i and S2i from S1 and S2, respectively, represent the voltage and current parameters before and after the disturbance, providing reliable data support for subsequent equivalent model construction and loop closing current calculations.

3.2.  Equivalent model construction method for distribution networks based on Thevenin’s theorem

In practice, distribution networks often include multiple distributed generators and loads, making the network structure highly complex. If detailed modeling methods are used to construct node matrices, any fluctuation or structural change at a node will complicate the calculation process. To address this, this paper adopts an equivalent model construction method based on Thevenin’s theorem, with the basic principle illustrated in Figure 3. This equivalent modeling method divides the complex distribution system into external and internal systems. The external system, corresponding to the distribution network, is simplified into a series combination of open-circuit voltage and equivalent impedance through equivalent processing. The internal system covers the loop closing point and nearby distributed generation and loads, serving as the disturbance source to capture the dynamic changes in the external system.

FIGURE 3  Topology structure of distribution networks and its equivalent model construction method

Assuming a disturbance occurs in the internal system on the left side of the loop closing point, the dynamic monitoring module captures the voltage and current parameters at the point of common coupling (PCC) before and after the disturbance, marking historical data as and , and recent data as  and . Considering that the impedance of the external system remains unchanged during the disturbance in the internal system, its calculation formula is:

（1）

The equivalent impedance Zeq1 represents the overall electrical characteristics of the external system and can be updated in real time after system fluctuations, accurately reflecting the dynamic behavior of the grid under different disturbance conditions.

The open-circuit voltage can be determined using Thevenin’s equivalent theorem based on the current electrical parameters, combined with the equivalent impedance calculation, and its formula is:

（2）

The open-circuit voltage reflects the system’s steady-state characteristics before and after the disturbance and the voltage distribution after the disturbance ends.

For the internal system, if the disturbance source is a load variation located near the loop closing point, the line impedance can be ignored. In this case, the load variation does not affect the voltage at the loop closing point, and the open-circuit voltage and equivalent impedance remain unchanged, i.e., Zeqa = Zeq1, and .

When the disturbance source is a fluctuation in the distributed generation, the system can be equivalent to a series combination of an equivalent voltage source  and internal impedance ZDG. The distributed generation is then in parallel with the external system, and the formulas for the equivalent impedance and open-circuit voltage are as follows:

（3）

（4）

This equivalent method effectively simplifies the computational process of complex distribution networks while ensuring that the system can dynamically reflect the uncertainties of distributed generation and loads, thereby providing robust model support for the accurate calculation of loop closing current.

4.  Loop closing current calculation method for distribution networks

4.1.  Steady-state current calculation

The steady-state loop closing current refers to the current induced by the voltage difference between the two ends after the loop closing operation has stabilized. Its calculation requires an accurate assessment of the equivalent impedance and open-circuit voltage on both sides of the loop closing point. Under steady-state conditions, the loop closing current can be calculated using the following formula:

（5）

During the steady-state current calculation, the voltage and current monitoring mechanism from the dual-stack structure can be used to obtain real-time changes in the voltage difference and impedance at the loop closing point, ensuring high accuracy and adaptability in the current calculation. Additionally, the magnitude of the steady-state current is not only dependent on the voltage difference at the loop closing point but also on the equivalent impedance. In practice, changes in grid topology and system load will impact the electrical characteristics at the loop closing point, altering the distribution of the loop closing current. Therefore, real-time updates of the impedance and voltage difference at the loop closing point are crucial for accurate steady-state current calculation.

4.2.  Transient (Inrush) Current Calculation

Transient (inrush) current refers to the momentary surge in current caused by transient system characteristics during the loop closing operation. The sudden change in voltage difference during the loop closing operation leads to a transient response from internal power sources and loads, generating a significant inrush current, which is especially notable in complex distribution networks containing distributed generation.

Typically, the maximum instantaneous value of the loop closing current occurs approximately half a cycle (0.01s) after the loop closing operation. The maximum effective value of the inrush current can be calculated as:

（6）

Where Ist is the effective value of the steady-state current, and Ta is the time constant of the non-periodic component of the loop closing current, which reflects the decay process from transient to steady state.

To calculate the inrush current, the optimal frequency method can be employed to determine the decay time constant Ta. This method analyzes the impedance characteristics of the system at a specific frequency fc, converting the equivalent impedance at the nominal frequency fn to the impedance Zeq(fc) at fc as follows:

（7）

For a 50Hz grid, the optimal frequency fc is typically set to 20Hz. At this frequency, the system’s inductive and resistive characteristics can effectively describe the inrush current decay process. The decay time constant Ta can then be calculated as:

（8）

Compared to other existing methods, the optimal frequency method is applicable to grid impedance ratios ranging from 0.005 ≤ R/X ≤ 5.0, making it suitable for a wide range of scenarios. Moreover, this method significantly enhances the accuracy of inrush current calculation under complex source-load conditions, particularly in distribution networks with high dynamic variability, ensuring the precision and reliability of current calculations during loop closing operations.

FIGURE 4  Schematic diagram of the loop closing current calculation process in distribution networks

Based on this, the loop closing current calculation method proposed in this paper can be summarized into four steps, as shown in Figure 4:

- Based on the disturbances in the internal system, use the dynamic monitoring system with a dual-stack structure to obtain the voltage and current data at the PCC before and after the disturbance;

- Calculate the equivalent impedance and open-circuit voltage of the external system using Equation (1) and (2). When the internal system contains distributed generation (such as PV), further calculations are required using Equation (3) and (4) to construct the equivalent model of the entire distribution system;

- Use the equivalent impedance and open-circuit voltage of both systems as inputs and calculate the steady-state current using Equation (5);

- Apply the optimal frequency method to determine the equivalent impedance at the specific frequency fc using Equation (7) and calculate the inrush current decay time constant Ta using Equation (8), then obtain the inrush current using Equation (6). The entire process integrates dynamic monitoring and equivalent modeling to accurately calculate both steady-state and inrush currents in the distribution network, providing reliable technical support for loop closing operations in real-world power grids.

5.  Simulation example analysis

5.1.  Simulation scenario setup and parameter configuration

Taking a specific loop closing network as an example, the network topology and the distribution of distributed generation (DG) and loads are shown in Figure 5. This loop closing network consists of multiple feeders, each with an impedance of (0.11+j0.15) Ω/km, and the lengths of the feeders are marked in the figure. The load power at each node is measured in MVA, and the maximum output power of the distributed photovoltaic (PV) systems PV1 and PV2 is 1.45 MW. Before loop closing, the line voltage of bus 1 is 34.30∠-3.4°kV, and the line voltage of bus 2 is 35.70∠2.2°kV. The distribution of sources and loads in the figure fully considers the diversity and dynamics of real-world power grids, effectively simulating the impact of source-load fluctuations on the loop closing current.

FIGURE 5  Schematic diagram of the distribution network loop closing example

5.2.  Analysis of loop closing current characteristics under distributed generation and load uncertainty

This section analyzes the impact of source-load uncertainty on loop closing current, focusing on the variation trends of loop closing current under different load and PV output conditions. First, by reducing the load on L2, changes in loop closing current under varying load conditions are observed, as illustrated in Figure 6(a), with corresponding data provided in Table 1. Subsequently, adjustments to the output power of PV1 result in changes in loop closing current due to reduced PV output, as shown in Figure 6(b).

The simulation results indicate that the bus voltage at B2 is higher than that at B1, and the phase of B2 leads B1, resulting in the loop closing current flowing from PCC2 to PCC1. When the PV output decreases, the active power supply in the system reduces, causing an increase in the voltage difference across the loop closing point, thereby raising the loop closing current. Similarly, as the load power on L2 decreases, the shunt effect at the loop closing point weakens, leading to a further increase in loop closing current. These results demonstrate that fluctuations in distributed generation and loads significantly affect loop closing current. Therefore, in practical operations, it is essential to account for source-load uncertainty to ensure accurate loop closing current calculations and provide reliable data for proactive loop closing decisions.

(a) Load L1 power fluctuation

(b) PV1 output fluctuation

FIGURE 6  Loop closing current waveform under different source and load fluctuations

TABLE 1  Voltage difference and loop closing current under various source and load fluctuations

| Scenario | Voltage difference/V | Phase difference /° | Steady current /A | Impact current/A |
| --- | --- | --- | --- | --- |
| Intial L2 | 1589.80 | 4.18 | 277.49 | 282.67 |
| 50% L2 | 1725.79 | 4.32 | 291.10 | 296.52 |
| No L2 | 1862.45 | 4.46 | 304.94 | 310.64 |
| 100MW PV1 | 1589.80 | 4.18 | 277.49 | 282.67 |
| 50MW PV1 | 1640.62 | 4.36 | 288.91 | 294.17 |
| No PV1 | 1686.04 | 4.69 | 290.25 | 295.62 |

5.3.  Verification of equivalent modeling under source-load disturbances

This section analyzes the accuracy of the external system’s equivalent model under source-load disturbances. Taking the left-side external system in Figure 5 as an example, the external system is set up with three conditions: the original system state, the addition of a three-phase balanced load (0.61+j0.14MVA) at L1, and the addition of an AB-phase unbalanced load (0.61+j0.14MVA) on top of condition 2. Within the internal system, disturbances are first applied to PV2, and then PV2 is replaced by L3 to evaluate the equivalent model's performance under different conditions.

To obtain the equivalent model of the external system, disturbances are applied to the internal system. First, the irradiance of PV2 is adjusted to disturb the internal system. Next, PV2 is replaced by L2, and the load power of L2 is altered to apply further disturbances. The equivalent impedance and open-circuit voltage of the left-side external system are finally calculated, as shown in Figure 7, with the results provided in Table 2.

(a) Equivalent Resistance

(b) Equivalent Reactance

(c) Line Voltage

(d) Voltage Phase

FIGURE 7  Characteristics of the external system's equivalent model under different source-load fluctuations

TABLE 2  Equivalent model calculation results under different disturbance scenarios

| Parameter | PV fluctuation |  |  | Load distribution |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | C1 | C2 | C3 | C1 | C2 | C3 |
| Resistance/Ω | 3.35 | 3.30 | 2.91 | 3.33 | 3.32 | 2.89 |
| Reactance/Ω | 3.19 | 3.21 | 2.40 | 3.16 | 3.17 | 2.43 |
| Voltage/kV | 33.98 | 33.97 | 23.95 | 33.98 | 33.79 | 23.90 |
| Angle/° | -3.83 | -3.89 | -12.31 | -3.85 | -4.06 | -12.56 |

The simulation results show that when the external system changes, the proposed equivalent modeling method can accurately calculate the equivalent impedance and open-circuit voltage of the external system, verifying the effectiveness of the method under different disturbance conditions. Furthermore, regardless of the disturbance method applied to the internal system, the equivalent modeling results under different conditions exhibit high consistency, demonstrating that the proposed modeling method can maintain accuracy in calculating equivalent impedance and open-circuit voltage under various disturbance scenarios.

5.4.  Verification of loop closing current calculation

This section verifies the accuracy and effectiveness of the loop closing current calculation method. The simulation scenario is set up with distributed PV2 connected to the left side of the loop closing point and load L3 connected to the right side. During the simulation, the left-side external system establishes an equivalent model by simulating the irradiance fluctuation of PV2, where PV2 and the external system form a parallel configuration of two active systems. The right-side external system simulates L3 load power disturbances to establish an equivalent model, represented by a typical voltage source and series equivalent impedance. Based on the equivalent models of the systems on both sides of the loop closing point, the steady-state and impact currents are calculated, as shown in Figure 8, with the simulation data provided in Table 3.

(a) Effective value of loop closing current

(b) Phase of loop closing current

FIGURE 8  Waveform of loop closing current based on the equivalent model of the closing system

TABLE 3  Simulation results of steady-state and impact currents at the closing point

| Parameter | Calculated value | Actual value | Error |
| --- | --- | --- | --- |
| Steady current | 281.00A | 281.87A | 0.31% |
| Impact current | 287.16A | 286.84A | 0.11% |
| Current phase | -162.87° | -160.64° | 1.39% |

The simulation results show that the equivalent model and loop closing current calculation method achieve errors of 0.31%, 0.11%, and 1.39% in steady-state current, impact current, and current phase, respectively, all within a reasonable range. This demonstrates the high calculation accuracy of the proposed model and method, providing robust support for loop closing current calculations in complex distribution networks.

5.5.  Verification of dynamic monitoring efficiency

To verify the effectiveness of the dynamic monitoring module in loop closing current calculation, PV2 is replaced with a network-structured PV system, and steady-state and impact current calculations are performed. The results are shown in Figure 9. As can be seen from the figure, due to the low inertia of the PV system, significant oscillations in the current waveform occurred after the loop closing operation. However, the proposed method detected this oscillation waveform through the dynamic monitoring module and tracked the steady-state current in real time. The results show that the steady-state current calculation values are still in good agreement with the actual measured values, validating the method's stability and dynamic response capability under complex operating conditions.

FIGURE 9  Loop closing current waveform under system oscillation conditions

6.  Conclusion

To address the challenges in loop closing current calculations in distribution networks, this paper proposes an online loop closing current calculation method based on a dual-stack dynamic monitoring system, which effectively handles source-load fluctuations in complex distribution networks. The following conclusions are drawn from the study and simulation results:

- The proposed method utilizes a dual-stack dynamic monitoring module, providing real-time monitoring and recording capabilities to accurately capture system dynamic changes. In scenarios with frequent source-load fluctuations, the method demonstrates a high response speed, significantly enhancing the real-time responsiveness of the loop closing current calculation process.

- By adopting an equivalent modeling approach, this method simplifies the complex structure of distribution networks, reducing the computational difficulty of loop closing current calculations. The model construction fully considers the impact of distributed generation and load integration on the dynamic characteristics of the grid, offering a more comprehensive reflection of the system’s operational state. This improvement enhances the method’s adaptability in scenarios involving distributed generation integration and frequent load variations.

- The method achieves a comprehensive analysis of loop closing current by calculating both steady-state and impact currents. The application of the optimal frequency method to determine the equivalent impedance and attenuation time constant at a specific frequency further improves the accuracy of impact current calculations. Simulation results show that the error in steady-state and impact current values is controlled within 0.5%, and the phase error is within 1.5%. This demonstrates the method’s high applicability and precision under complex conditions, providing effective guidance for actual loop closing operations in power grids.

Acknowledgement

This paper is supported by the Headquarters Management Science and Technology Project of the State Grid Corporation of China. The funding project is titled "Research and Demonstration of Key Technologies for Loop Closing Strategy Evaluation and Active Control in Large Urban Power Grids Adapted to Distributed Power Integration" (Project No. 5100-202311424A-3-2-ZN)

References

[1]	Yuan, H., Li, F., Wei, Y., et al.: Novel linearized power flow and linearized OPF models for active distribution networks with application in distribution LMP. IEEE Trans. Smart Grid 9(1), 438–448 (2018).

[2]	Xing, X., Lin, J., Wan, C., et al.: Model predictive control of LPC-looped active distribution network with high penetration of distributed generation. IEEE Trans. Sustain. Energy 8(3), 1051–1063 (2017).

[3]	Lin, Z., Hu, Z., Song, Y.: Distribution network expansion planning considering N-1 criterion. IEEE Trans. Power Syst. 34(3), 2476–2478 (2019).

[4]	Yan, X., Peng, W., Wang, Y., et al.: Flexible loop closing control method for an active distribution network based on dual rotary phase shifting transformers. IET Gener. Transm. Distrib. 16(20), 4204–4214 (2022).

[5]	Jiang, X., Pan, P., Wang, H., et al.: Static equivalence method of power grid based on genetic algorithm. Electronics 13(9), 1647 (2024).

[6]	Burchett, S.M., Douglas, D., Ghiocel, S.G., et al.: An optimal Thévenin equivalent estimation method and its application to the voltage stability analysis of a wind hub. IEEE Trans. Power Syst. 33(4), 3644–3652 (2018).

[7]	Sheng, W.: Partition decoupling model and method in power distribution network, part I: Optimised network partition model and process. IET Cyber-Phys. Syst. Theory Appl. 8(1), 43–51 (2023).

[8]	Yun, Z., Cui, X., Ma, K.: Online Thevenin equivalent parameter identification method of large power grids using LU factorization. IEEE Trans. Power Syst. 34(6), 4464–4475 (2019).

[9]	Fang, J., Deng, H., Goetz, S.M.: Grid impedance estimation through grid-forming power converters. IEEE Trans. Power Electron. 36(2), 2094–2104 (2021).

[10]	Huang, B., Li, Z., Zheng, J., et al.: Probabilistic active distribution network equivalence with correlated uncertain injections for grid analysis. IET Renew. Power Gener. 14(11), 1964–1977 (2020).

[11]	Abapour, S., Zare, K., Mohammadi-Ivatloo, B.: Dynamic planning of distributed generation units in active distribution network. IET Gener. Transm. Distrib. 9(12), 1455–1463 (2015).

[12]	Conte, F., D’Agostino, F., Silvestro, F.: Operational constrained nonlinear modeling and identification of active distribution networks. Electric Power Syst. Res. 168, 92–104 (2019).

[13]	Luo, X., Cao, S., Hu, C., et al.: Study of calculation method of current induced by closing-loop operations based on PMU in distribution networks with DG. In: 2020 5th Asia Conf. Power Electr. Eng. (ACPEE), pp. 1668–1674 (2020).

[14]	Zheng, C., Wang, S., Liu, Y., et al.: A novel RNN based load modelling method with measurement data in active distribution system. Electric Power Syst. Res. 166, 112–124 (2019).

[15]	Wang, P., Zhang, Z., Huang, Q., et al.: Robustness-Improved method for measurement-based equivalent modeling of active distribution network. IEEE Trans. Ind. Appl. 57(3), 2146–2155 (2021).

[16]	Golpîra, H., Seifi, H., Haghifam, M.R.: Dynamic equivalencing of an active distribution network for large-scale power system frequency stability studies. IET Gener. Transm. Distrib. 9(15), 2245–2254 (2015).

[17]	Cheng, Y., Wu, W., Yang, Y., et al.: Zero-sequence voltage injection-based grid impedance estimation method for three-phase four-wire DC/AC Grid-Connected Inverter. IEEE Trans. Ind. Electron. 71(7), 7273–7279 (2024).

[18]	Hoffmann, N., Fuchs, F.W.: Minimal invasive equivalent grid impedance estimation in inductive–resistive power networks using extended Kalman filter. IEEE Trans. Power Electron. 29(2), 631–641 (2014).

[19]	Zhang, K., Feng, Y., Yu, Y., et al.: Study of calculation schemes of currents induced by closing-loop operations in medium-voltage distribution grids. In: 2019 IEEE Sustainable Power and Energy Conf. (iSPEC), pp. 2488–2493 (2019).

[20]	Xiaoqing, H., Yuan, N., Putong, W., et al.: Calculation method of closed-loop current in distribution network based on the improved cumulant method. In: Annual Meeting of CSEE Study Committee of HVDC and Power Electronics (HVDC 2023), pp. 376–383 (2023).

[21]	Qiu, Z., Wu, L., Zeng, T., Yuan, W., Zhang, X., Cheng, T.: An efficient sparse matrix technique for closed loop current analysis in distribution network. In: 2022 5th Int. Conf. Renew. Energy Power Eng. (REPE), pp. 222–227 (2022).

[22]	Li, M., Huang, W., Tai, N., et al.: Surge current calculation and limit strategy of the IIDG during loop closing operation in distribution networks. In: 2019 IEEE Sustainable Power and Energy Conf. (iSPEC), pp. 756–761 (2019).

[23]	Luo, X., Yang, J., Gu, L., et al.: Research on closing-loop current calculation method and control strategy in complex distribution network. In: 2020 IEEE/IAS Ind. Commercial Power Syst. Asia (I&CPS Asia), pp. 992–999 (2020).

[24]	Wang, H., Yu, X., Zhang, Z., et al.: Calculation, measurement and engineering application Of loop closing current in power grid. In: 2021 IEEE 5th Conf. Energy Internet Energy Syst. Integr. (EI2), pp. 2237–2241 (2021).