Date of publication xxxx 00, 0000, date of current version xxxx 00, 0000.

Digital Object Identifier 10.1109/ACCESS.2024.Doi Number

Optimizing vital nodes detection in complex distribution networks with a global structural model

Lingyun Wang1, Yang Li1, Honglei Xu2, Ran Li1, and Yushan Zhou1

1 College of Electrical Engineering and New Energy, China Three Gorges University, Yichang 443002, Hubei Province, China;

2 School of Electrical Engineering, Computing and Mathematical Sciences, Curtin University, Perth, WA, 6845, Australia

Corresponding author: Yang Li (e-mail:nail0624ly@gmail.com).

This work was supported in part by the National Natural Science Foundation of China Grant.

ABSTRACT The identification of vulnerabilities within distribution networks, impacted by complex factors such as ring configurations and the integration of distributed energy resources, remains a significant challenge. This study presents a novel enhanced hierarchical analysis fault chain comprehensive assessment model to address this issue. The proposed model develops four new weak indicators of assessing the nodes of a distribution network based on complex network theory: an improved indicator of node degree, improved indicator of node PageRank, power flow increment impact indicator, and node voltage stability indicator. It introduces the weighting method with the binomial coefficient for optimal distribution of weight in the fault chain framework to further enhance effectiveness in refined hierarchical analysis, aimed at improving objectivity and precision. Besides, it employs an Integrated Analytic Hierarchy Process in which system indicators and operational parameters under various conditions can be integrated and dynamically calculate the fault rate of a weak link in the network. These further enhance the adaptability and precision of the model in solving inherent complexities within modern distribution networks. Simulation case studies performed using IEEE-69 node complex active distribution network have demonstrated the efficacy and superiority of the proposed method for correct identification of weak nodes.

INDEX TERMS Weak node identification, complex distribution network, complex network theory, Fault Chain Model, distributed generation.

INTRODUCTION

In the last few decades, distribution networks became more and more complex due to the increase in demand for sustainable power sources such as Distributed Generators  and electric vehicles [1,2]. Traditional radial distribution networks are inadequate for accommodating the large-scale integration of distributed energy resources [3,4]. To enhance resilience against various disturbances, loop network designs, which create multiple supply paths, have been implemented globally. Notable examples include the petal-type network in Singapore, the "triple-double" (dual-side power, dual trunk, dual access) network structure in Paris, France, and the diamond-type medium-voltage network structure in Shanghai, all of which exemplify successful applications of ring network configurations [5]. These designs not only improve power supply redundancy but also enhance the grid's fault responsiveness and overall resilience. However, the integration of DGs and the adoption of loop network designs introduce new complexities and challenges to distribution networks [6,7]. These configurations increase the network's complexity and uncertainty, particularly impacting the dynamic balance of the grid in response to the unpredictability associated with DGs. Therefore, it is importance to research into the vulnerabilities of complex distribution networks. Such systematic identification followed by further analysis may provide a strong theoretical framework and simultaneously serve to guide the best-possible design, risk assessment, and safe operation of power grids.

Most of the existing literature on node frailty identification is based on complex network theory [8]. Wu et al. [9] proposed a structure vulnerability analysis technique for a power system that recognizes weak links by analyzing the topological structure of the grid. It contains both static and dynamic analysis approaches, as well as time-domain simulations to carry out a thorough system vulnerability assessment. In this respect, for the analysis of power grid networks, Luo et al. [10] addressed the hierarchical structural attributes and their relation to the correlation of vulnerability analysis. Xiao et al. [11] proposed a novel method to propose a node vulnerability assessment system by combing the theory of complex networks with game theory, considering not only the structure of the distribution network but also the running state of the system. Zhou et al. [12] presented a model of the evaluation, from which three view hierarchies can be drawn: one in view of the grid topological structure, another concerning the current operation status of the system, and one due to the consequences of the failures of nodes; such hierarchical node vulnerability indices can present deeper analyses on the inter-relationships among such criteria. The newly proposed cascade fault model was the first in analyzing possible overload problems with impact nodes and edges [13]. The research provided a method that showed a suitable index of how to evaluate cascade damage and a cascade destruction process using an electrical grid: system salience, and system destruction-optimization models in goal-setting to allocate important grids by assigning values. This ranked orders in relation to regret values. However, much of the research up to now has been based on some experience or subjective judgments on the importance of the node indicator and often leads to inaccuracies in the assessment results. This kind of approach, though it requires quite a lot of expertise and is labor-intensive, is bounded by such shortcomings in practical engineering applications.

This study proposes Integrated Analytic Hierarchy Process-Fault Chain Model (IAHP-FCM) to overcome the deficiencies of traditional methods. This multidimensional evaluation model is designed to accurately represent the vulnerabilities of network nodes by considering various factors, such as the topology of the network defined by electrical buses and their interconnections, along with operational conditions like supply and demand distributions. In order to reduce the influence brought about by subjective judgment from independent experts, Analytic Hierarchy Process is used to determine the weights of FCM, which is then optimized using the binomial coefficient weighted sum model. To prove the effectiveness of the proposed model, this research conducts analyses by means of real-world data from IEEE-69 distribution network that encompasses DGs and loop network designs.

NEW DISTRIBUTION NETWORK NODE WEAKNESS INDICATORS

A network G is comprised of nodes, edges, and weights, as described for complex network theory [14,15]. A fundamental characteristic of a node degree v indicates the number of connections to other nodes. In directed graphs, these connections are categorized into in-degree and out-degree, representing incoming and outgoing connections, respectively. In FIGURE 1,  the network includes a green node G as the engine node, a yellow node L as the load node, and a red node E that represents a DG or energy storage element. The arrows in FIGURE 1 indicate the direction of energy flow between the nodes. Even systems with identical nodal degrees for load nodes can exhibit differing in-degrees and out-degrees, which are contingent upon the operational phase.

(a) A normal operating situation

(b) Another normal operating situation

Energy transmission relationship among power grid nodes.

In general radial networks, the impact of in-degree and out-degree on node degree is relatively minor. Conversely, in weighted power networks that include DG or ring configurations, this impact becomes significant.

- IMPROVING NODE DEGREE INDICATOR

In the field of complex network theory, the calculation for traditional node degree, which considers both in-degree and out-degree, is presented as follows:

(1)

where n is the total number of nodes in the system; mij is the power flow from node i to node j; and mji is the power flow from node j to node i. Equation (1) is further optimized by integrating power injection and the loop network ratio into the calculation.

(2)

where Pi is the injected power of node i; Sb is the system base power; H is the total number of rings in the system. H=1 if the system does not have ring network; hi is the number of rings in which node i is located; and the addition of 1 prevents zeroing, which can occur when certain nodes are located on branches outside the ring network.

To more effectively elucidate the interactions between nodes within a network affect in contributing to network vulnerabilities, this study introduces a revised node importance method. This method is based on the calculation of network vulnerability for K-1 events [16] and is informed by the principles of Laplacian matrix theory from graph theory. The enhanced calculation of node importance is presented in the following equation:

(3)

(4)

where L(G) is Laplacian matrix of network G; D(G) is the vertex degree diagonal matrix of network G, with its elements corresponding to the node degrees D(i) for each node; A(G) is the adjacency matrix of network G; ρ(L(n)) is the spectral radius of Laplacian matrix before the network change; and ρ(L(n-i)) is the spectral radius of Laplacian matrix after the removal of node i from the network. The improved node degree indicator DL(i) reflects the interaction between the local and global characteristics of the nodes. Its magnitude indicates the extent to which a node impacts the system's overall weakness. A higher DL value signifies greater node impact within the network. In the event of a cyberattack, nodes with higher DL(i) values could significantly compromise network stability by reducing overall connectivity, thereby increasing system fragility.

- IMPROVING NODE PAGERANK METRICS

PageRank, an adaptation of eigenvalue centrality, assesses the significance of a node by recursively analyzing the number of incoming edges and PageRank values of the connected nodes [17]. Despite its advantages, PageRank has certain limitations when applied to specialized domains such as power systems, particularly for directed networks [18].  To mitigate these challenges, the method integrates improved metrics for node degree and connected decay factors, which are particularly effective for managing complex ring network structures in power systems. These enhanced PageRank metrics offer a more accurate representation of a node's role and importance within the overall network architecture. The calculation of this indicator is articulated as follows:

(5)

where PR is the improved PageRank centrality of node i; A is the system adjacency matrix; DL (j) is the improved node degree of the connected node; β is the out degree of the connected node; and α is the connected attenuation factor, its value decreases with the increase of the number of spaced nodes between node i and node j. Given that a significant number of nodes in the distribution network are located on single branches, this study focuses only on directly connected nodes when analyzing node importance, setting α=1. β serves as an offset to prevent situations where nodes with only out-degrees cause the iteration score to converge to 0. A higher PR value indicates stronger node centrality. In the event of a system attack, the failure of nodes with high centrality renders the network more fragile, leading to a more severe impact on overall system stability.

- IMPROVING INCREMENTAL POWER FLOW IMPACT ANALYSIS

The growing incorporation of DG within distribution networks has led to increased uncertainty in DG output, thereby adding complexity to power system operations, especially in response to external disturbances. In practical applications, the majority of DG units are primarily oriented towards serving the load side, with the objective of optimizing utility by meeting load demands. This operational focus subsequently impacts the disturbance resilience of each node within the system. To evaluate the impact of DG output uncertainty on the overall distribution network under realistic conditions, this study employs utility theory from economics to analyze the severity of incremental trends associated with fluctuations in DG output [20].

This study examines a distribution system consisting of n nodes and l lines. Under standard operating conditions, the system is designated as state 0. An increase in load at the ith node results in a corresponding rise in system current, which is expressed as follows:

(6)

where Pk (i) is the current of the kth line when the load unit of the ith node increases and Pk_0 is the current of the kth line during normal operation (i.e., state 0). In distribution systems, the probability of line failure associated with a node increases with the magnitude of the incremental current and the node's susceptibility to disturbances, thereby amplifying the system's vulnerability. The impact of such incremental shocks on system stability is quantitatively evaluated using a risk-preference utility function derived from economics as follows:

(7)

The utility function within Equation (7) must adhere to the constraints (Se(i)'>0, Se(i)''>0), where Se represents the indicator of the incremental impact of the power flow at node i. A larger value of Se suggests that, under the incremental impact of the current power flow within the system, there is an increased likelihood of failure at node i, a more rapid decline in anti-jamming capability, and a greater degree of vulnerability within the system.

- NODAL VOLTAGE STABILIZATION INDICATOR

Jasmon et al. [21] developed a voltage stabilization index specifically for distribution networks. However, this index demonstrates limited adaptability and is prone to significant errors in both radial and ring-containing distribution networks. To address these shortcomings, Wu et al. [22] proposed an enhanced static voltage stability determination index for distribution networks, which effectively improves the applicability of the voltage stability index in radial distribution grids. However, its effectiveness in ring-containing distribution grids remains moderate. To further enhance the applicability of these indicators, this study refines the voltage stability indicators for distribution network nodes by employing a method that evaluates the existence of power flow solutions. In calculating the voltage equations for these nodes in Wu et al. [22], it is essential that the root discriminant of the equations satisfies the following condition:

(8)

where Ui is the voltage at node i; Pj and Qj are the active and reactive powers at node j, respectively; while Rij and Xij are the line resistance and reactance between nodes i and j, respectively. Accordingly, the voltage stability index Lij for distribution network branches is defined based on power flow solutions as follows:

(9)

To improve the applicability of this index for network systems that include rings, an optimization process is implemented to assess the weakness level Ln of the nodes within the distribution network:

(10)

An increase in the value of Ln signifies that the node is approaching the voltage collapse branch, which is associated with a decline in the voltage stability of that branch. Additionally, the stability of the nodes located at both ends of the branch is also adversely impacted.

DISTRIBUTION NETWORK WEAK POINT IDENTIFICATION MODEL

- MODELING POTENTIAL FAILURES THROUGH FRAMEWORK OF ACCIDENT CHAINS

In the event of a failure at a specific node within the power supply system, the overall power flow is altered, which may lead to overload conditions in other lines and, consequently, disconnections that can trigger cascading failures. To ensure that the simulated cascading failures encompass a broad spectrum of potential scenarios, this study employs FCM. This model facilitates the sequential designation of each node in the power grid, which is assumed to consist of n lines, as the initial point of failure. AHP is utilized to ascertain the failure weights, simulate the points of cascading failure, and generate n accident chains for the purpose of examining and analyzing the various potential results of cascading failures. The comprehensive process of cascading failure is depicted in FIGURE 2.

Flowchart of system chain failure accident chain model.

Significant losses within the power system are often linked to large-scale blackout events, which can result from a multitude of factors and may have substantial implications for the economy, social functions, and the daily lives of individuals. As outlined in "Interim Regulations on the Investigation of Power Production Accidents" (National Energy Administration's Order No. 4), a threshold for load loss has been established at 40%. This provision indicates that when the system experiences a cascading failure leading to a load loss equivalent to 40% of the grid's total load, or if three incidents occur in succession in relation to the cascading failure, the accident chain model will terminate the simulation of that specific accident chain.

Calculation of Line Load Ratio

To effectively utilize the load capacity of the power supply line alongside the actual operational load, it is imperative to collect data regarding the load associated with the power supply line. Following this, a calculation equation should be formulated to ascertain the load rate ε of the power supply line.

(11)

(12)

where PN is the rated power of the power supply line; P0 is the input power of the power supply line when it is not loaded; PS_l is the actual operating power of the power supply line designated as l; PN_loss is the power dissipated by the power supply line under conditions of rated load operation (Equation (12)); Pdata is the overall load magnitude of the system; and λ is the ratio between the load capacity and the actual load within the power supply line.

Calculation of Line failure rate

This paper presents a comprehensive analysis of the local characteristics, overall topology, power transmission efficiency, and voltage stability within the power distribution network. It employs AHP to establish a hierarchical framework and evaluates the fault rates of lines across various operational scenarios [23]. To address the challenges related to excessive subjectivity and model fitting inherent in AHP, this study proposes several enhancements:

(a) The construction of a judgment matrix at the criterion level can be enhanced through the implementation of secondary optimization using Binomial Coefficient Weighted Sum Method (BCWSM). This approach significantly improves the representation of expert experience within the judgment matrix, thereby effectively mitigating the subjectivity inherent in AHP.

Consistency testing is essential for assessing whether the matrix exhibits an acceptable Consistency Ratio (CR) in Equation (14), where RI is the average random consistency index, which is contingent upon the order m of the judgment matrix. A CR value of less than 0.1 signifies satisfactory consistency within the matrix. Furthermore, a judgment matrix that attains a higher level of consistency contributes to the reliability of the decision-making process. A lower CR value allows decision-makers to have increased confidence in the weights derived from AHP method.

(13)

This method is well-suited for addressing multi-objective decision-making challenges that do not depend on weighted experiences. By synthesizing the insights of multiple experts, the contributions of these experts can be more accurately represented in the judgment matrix, thereby reducing the subjectivity inherent in AHP. The optimization strategy employed by BCWSM involves a systematic analysis of the significance of a set of objectives as evaluated by experts, followed by a symmetrical pairwise comparison. The entire ranking procedure employs a complex cyclic comparison technique, in which each pair of objectives is assessed twice, requiring each expert to conduct a total of (a-1) comparisons. Upon completion of the comparisons by all experts, the average values of the objectives are calculated.

(14)

where p(Li) is the priority number of target Li; q(Li) is the number of times the target Li is prioritized; k is the number of experts; and  is the average target value, which is prioritized from the set of targets and then processed using the binomial coefficient weighting method to obtain the comprehensive target value R(Li). Finally, the ninescale method is applied to incorporate the comprehensive target value into the secondary construction of the judgment matrix. The calculation for comprehensive target value is expressed as follows:

(15)

(b) The adjustment of objectives at the scheme level necessitates the conversion of these objectives into quantifiable data associated with system nodes. This transformation replaces vague subjective evaluations with objective metrics relevant to the weak indicators linked to each node. The process involves the integration of system parameters across diverse operational conditions, thereby improving the weight calculation method of AHP concerning the failure rates of dynamic weak links within the distribution network. As a result, this approach seeks to enhance the model fit of AHP.

The complete IAHP is illustrated in FIGURE 3.

Flow chart of IAHP comprehensive evaluation model.

The calculation for the final line failure rate is presented as follows:

(16)

where w1, w2, w3, and w4 are the weights assigned to the four weak indicators of the system, as determined by IAHP under varying operational conditions; while DLmax, PRmax, Semax, and Lnmax are the maximum values of these four weak indicators, which are used to normalize each individual indicator, enabling a comprehensive evaluation of all indicators collectively.

Calculation of Node Weakness

The vulnerability of a node can be assessed by analyzing the losses incurred as a consequence of that node initiating a cascading failure, which is referred to as the initial failure event. If the formation of a failure chain consists of s stages, the anticipated failure of the fault chain ζi, instigated by node i, is determined by multiplying the probabilities of each failure occurring within the chain by their respective detrimental impacts. This calculation forms the foundation for evaluating the node's vulnerability, which can be expressed as follows:

(17)

where ε(l|si=k) is the probability of a fault in line l corresponding to stage k when node i causes a fault chain and C(ζi) is the load loss caused by node i on fault chain Zeta i.

- WEAKNESS IDENTIFICATION PROCESS

The analysis presented indicates that the process of identifying vulnerabilities within the power grid can be categorized into four stages as follows:

Step 1: Assess the power system's network structure and distributed generation operational states, and establish a weighted network topology.

Step 2: It is important to incorporate the complex network theory in the power flow analysis while studying the raw power grid data, which will be of immense help in retrieving very important system metrics such as initial load rate at every transmission line, failure rate of such transmission lines, the rate of loss of load, voltages measured, power measured, and other important indicators.

Step 3: The network and original data are input into FCM. Then, four improved indicators under various operation states are calculated based on FCM framework. After that, the improved indicators are input into IAHP to calculate the dynamic failure rate of the vulnerable links. Based on this, FCM can find the chain failure sequences with the highest risk.

Step 4: After simulating the chain failure sequences for all nodes, it is essential to conduct a quantitative assessment of the probabilities of failure, their severity, and the expected impacts associated with these failure chains. This analysis plays a crucial role in identifying the vulnerable nodes within the power grid.

CASE ANALYSIS

To validate the effectiveness of IAHP-FCM comprehensive assessment model, this study modifies the standard IEEE-69 node radial distribution network. The modifications involve increasing the number of branches to establish multiple rings and sequentially integrating five DGs at randomly selected nodes. The topology of the newly configured IEEE-69 node complex distribution network system is illustrated in FIGURE 4. This network operates at a nominal voltage of 12.66 kV with a base capacity of 100 MVA.

IEEE-69 node complex distribution network model.

For power flow calculations within distribution networks, nodes, with the exception of source nodes, are typically classified as PQ nodes. The integration of DG into the system may give rise to new node types within the distribution network, thereby impacting the results of power flow calculations. To facilitate the analysis, this section presents a summary of the power flow model for DG, which encompasses both PI nodes and PV nodes. However, for the purpose of simplifying power flow calculations, these nodes can ultimately be regarded as PQ nodes [24].

- APPLICATION FOR EVALUATING INTEGRATED MODELS OF IAHP-FCM

- First round simulation analysis of fault chain

The load rates and fault conditions of the power grid exhibit temporal variations. To develop effective management and optimization strategies for the power grid, an initial power flow calculation is conducted on the raw grid data. This calculation provides essential data and status information regarding the system (FIGURE 5).

Branch load rates in IEEE-69 distribution network after initial fault.

FIGURE 5 depicts the load distribution across the 78 branches within the system subsequent to the failure and deactivation of the initial 69 nodes. Notably, there is a significant increase in load within three specific sections of the system, particularly in the ranges of lines 1-15, 37-45, and 67-78. An analysis of the network structure in FIGURE 7 indicates that these ranges are linked to the ring network nodes, the backbone network, and the output branches of DG. Indeed, certain branches have already shown signs of overload.

- Construction of criterion layer judgment matrix

The nine-point scale method, utilized within the framework of AHP, facilitated the collaborative development of a criterion layer judgment matrix by a group of experts (TABLE 1). BCWSM was employed to improve the prioritization of the objectives, leading to the establishment of the judgment matrix on two occasions (TABLE 2).

- Expert criterion layer judgment matrix based on nine-point scale method.

|  |  | DL | PR | Se | Ln |
| --- | --- | --- | --- | --- | --- |
| Frst expert | DL | 1 | 1/2 | 1/5 | 1/6 |
|  | PR | 2 | 1 | 1/5 | 1/4 |
|  | Se | 5 | 5 | 1 | 1/2 |
|  | Ln | 6 | 4 | 2 | 1 |
|  | CR | 0.039079 |  |  |  |
| Second expert | DL | 1 | 1/5 | 1/6 | 1/9 |
|  | PR | 5 | 1 | 1/3 | 1/6 |
|  | Se | 6 | 4 | 1 | 3 |
|  | Ln | 9 | 6 | 1/3 | 1 |
|  | CR | 0.091752 |  |  |  |
| Third expert | DL | 1 | 3 | 1/4 | 1/6 |
|  | PR | 1/3 | 1 | 1/6 | 3 |
|  | Se | 4 | 6 | 1 | 1/3 |
|  | Ln | 6 | 7 | 3 | 1 |
|  | CR | 0.064668 |  |  |  |

- Optimized criterion layer judgment matrix using BCWSM.

|  | DL | PR | Se | Ln |
| --- | --- | --- | --- | --- |
| DL | 1 | 1/2 | 1/6 | 1/7 |
| PR | 2 | 1 | 1/3 | 1/5 |
| Se | 6 | 3 | 1 | 1/2 |
| Ln | 7 | 5 | 2 | 1 |
| CR | 0.010511 |  |  |  |

Based on CR values in TABLE 1,  the judgment matrix constructed by Expert 1 demonstrates the highest level of consistency, while the matrix developed by Expert 2 exhibits the lowest consistency. This observation underscores the considerable impact of individual subjectivity on the formulation of judgment matrices within AHP. In contrast, CR value of the judgment matrix at the criterion layer, following optimization by BCWSM (TABLE 2),  is significantly below 0.1. This result suggests that the optimization process implemented by BCWSM effectively enhances the consistency of the judgment matrix and substantially mitigates the excessive subjectivity associated with individual expert evaluations, thereby improving the overall reliability of the decision-making process.

Criterion level judgment matrix construction

After normalizing the results of the indicators, a program-level judgment matrix is constructed utilizing the nine-point scale method. The consistency test for this matrix is outlined in TABLE 3.

- Consistency test results of scheme layer judgment matrix.

| Programmatic layer consistency test | CR |
| --- | --- |
| Improvement of the node degree indicator | 0.008181 |
| Improvement of the node PageRank metrics | 0.001863 |
| Improvement of the node electrical dielectric index | 0.006313 |
| Improvement of the node electrical dielectric index | 0.007604 |
| Nodal Voltage Stabilization Indicator | 0.004425 |

CR for the judgment matrices at the programmatic level across all five indicators is below 0.1, suggesting that these matrices exhibit satisfactory consistency.

Example weak node identification results

The criterion level judgment matrix, scheme level judgment matrix, and network topology serve as inputs to IAHP-FCM assessment model. This model is employed to identify vulnerabilities within the newly configured IEEE-69 node complex distribution system.

- Consistency test results of scheme layer judgment matrix.

| Rank | Node | Weakness | Rank | Node | Weakness |
| --- | --- | --- | --- | --- | --- |
| 1 | 48 | 0.7499 | 11 | 20 | 0.0260 |
| 2 | 37 | 0.4597 | 12 | 10 | 0.0155 |
| 3 | 64 | 0.2822 | 13 | 27 | 0.0128 |
| 4 | 67 | 0.1753 | 14 | 3 | 0.0122 |
| 5 | 40 | 0.1295 | 15 | 42 | 0.0070 |
| 6 | 11 | 0.1119 | 16 | 36 | 0.0068 |
| 7 | 9 | 0.0861 | 17 | 47 | 0.0067 |
| 8 | 41 | 0.0652 | 18 | 56 | 0.0032 |
| 9 | 44 | 0.0450 | 19 | 62 | 0.0028 |
| 10 | 63 | 0.0368 | 20 | 57 | 0.0027 |

TABLE 4 delineates the top 20 weak nodes within the system, as identified by IAHP-FCM. The system topology in FIGURE 4 reveals that the higher-ranked weak nodes are predominantly situated in critical distribution areas. For example, Node 48, which is ranked highest, is positioned at multiple intersection points within the ring network and is vital for the overall functionality of the distribution network. An attack on these nodes could alter the system's topology, potentially resulting in failures of protective relays and other equipment. Furthermore, such an assault would directly impact the energy flow direction of two DG within the system, thereby indirectly impacting the output of the DGs and increasing the load on specific lines, which could precipitate more severe incidents. The model's capacity to accurately identify weak nodes in the newly established IEEE-69 node complex distribution network underscores its effectiveness and relevance in real-world complex distribution networks, significantly enhancing the precision of weak node identification.

- ANALYSIS OF NECESSITY AND SOPHISTICATION OF IAHP-FCM INTEGRATED ASSESSMENT MODE

- Analysis of model necessity

To assess the necessity and accuracy of IAHP-FCM introduced in this study, the comprehensive vulnerability level of each node was calculated independently using both the single indicator method and the proposed IAHP-FCM. This method enabled a comparative analysis of node vulnerability rankings across different assessment techniques. The research results are summarized in TABLE 5.

- Comparison of proposed method and single-index methods in node weakness ranking.

| Rank | DL | PR | Se | Ln | Proposed method |
| --- | --- | --- | --- | --- | --- |
| 1 | 27 | 3 | 3 | 27 | 48 |
| 2 | 54 | 4 | 2 | 12 | 37 |
| 3 | 20 | 11 | 1 | 39 | 64 |
| 4 | 39 | 36 | 59 | 53 | 67 |
| 5 | 12 | 66 | 62 | 45 | 40 |
| 6 | 38 | 12 | 61 | 52 | 11 |
| 7 | 57 | 37 | 60 | 63 | 9 |
| 8 | 2 | 2 | 63 | 9 | 41 |
| 9 | 1 | 67 | 4 | 46 | 44 |
| 10 | 52 | 57 | 65 | 49 | 63 |
| 11 | 69 | 68 | 64 | 11 | 20 |
| 12 | 53 | 59 | 49 | 24 | 10 |
| 13 | 51 | 65 | 48 | 15 | 27 |
| 14 | 9 | 64 | 68 | 48 | 3 |
| 15 | 4 | 63 | 50 | 64 | 42 |

TABLE 5 highlights significant differences in the vulnerable nodes identified using the single indicator method. This result supports the idea that each individual indicator reflects unique aspects of node vulnerability, which complicates the representation of the system's overall susceptibility.

For Se method, Node 3 ranks second in terms of flow increment impact indicators. However, its ranking is relatively lower when assessed through alternative methods. This observation may indicate that Node 3 demonstrates a heightened sensitivity to fluctuations in power flow, but it does not perform as well in other performance metrics. As a result, the evaluation of its weaknesses is significantly lessened following the model calculations presented in this study. In contrast, Node 27 is recognized as exhibiting the highest level of weakness in two single indicator methods, but its weakness ranking decreases to 12th place within the current method. Node 64 is positioned 14th and 11th in PR and Se methods, respectively, and does not attain high rankings in other approaches. However, its weakness escalates to 3rd place after the model calculations conducted in this research. This phenomenon can be attributed to the substantial impact that changes in the operational state of this node have on flow distribution within the system, leading to an imbalance of power flow in adjacent ring networks. Such imbalances may ultimately result in complications, including diminished voltage stability and angle instability at the node. This highlights that the method employed in this study provides a more comprehensive evaluation of node weaknesses by integrating structural vulnerabilities with the operational state of the network, thereby synthesizing multiple indicators.

This study aims to illustrate that IAHP-FCM not only preserves its inherent advantages but also substantially reduces the problem of excessive subjectivity. A comparative analysis is conducted between the traditional AHP and IAHP-FCM, drawing on a range of expert opinions. The results of this analysis are detailed in TABLE 1, with the results presented in FIGURE 6.

Weakness analysis and node comparison in IEEE69 distribution network.

FIGURE 6 illustrates the alignment of IAHP-FCM with the conventional AHP algorithm. This alignment is evidenced by the comparable trends observed in specific node intervals, including 1–14, 25–28, 36–39, and 49–56, which reveal significant vulnerabilities. Such similarities indicate a heightened concordance between these two methods in identifying critical weak nodes. However, a substantial divergence persists in the rankings of the majority of other nodes. This discrepancy can be attributed primarily to the traditional AHP's dependence on singular indicators and the subjective judgments of experts, which are susceptible to biases. Conversely, IAHP model mitigates the impact of subjective biases by incorporating multiple indicators, thereby providing a more objective and comprehensive assessment of node vulnerabilities. Furthermore, IAHP approach articulated in this research evaluates multiple indicators, lessening the impact of expert subjectivity on the model and more accurately reflecting the weak characteristics of nodes. When compared to the traditional AHP method, the results generated by IAHP for FCM are more precise and better suited for applications in engineering practice.

To improve the assessment of the adaptability of IAHP to the model proposed in this study, the initial expert decision that demonstrated the lowest CR value (TABLE 1), was employed to directly calculate the weak nodes within the system. This initial expert decision was subsequently integrated into the weak nodes of FCM calculation system, thereby establishing two control groups. The results obtained from IAHP-FCM method introduced in this paper were organized and analyzed, with a detailed presentation of the results in TABLE 6.

- Ranking comparison of AHP method and proposed method under different expert decisions.

| Rank | AHP (Specialist No. 1) |  | AHP-FCM (Specialist No. 1) |  | Proposed method |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Node | Weakness | Node | Weakness | Node | Weakness |
| 1 | 4 | 0.0567 | 3 | 0.0515 | 12 | 0.0471 |
| 2 | 11 | 0.0509 | 4 | 0.0485 | 27 | 0.0401 |
| 3 | 3 | 0.0498 | 11 | 0.0397 | 4 | 0.0354 |
| 4 | 12 | 0.0444 | 12 | 0.0381 | 11 | 0.0334 |
| 5 | 9 | 0.0311 | 66 | 0.0253 | 3 | 0.0324 |
| 6 | 10 | 0.0293 | 27 | 0.0233 | 39 | 0.0308 |
| 7 | 13 | 0.0281 | 9 | 0.0228 | 9 | 0.0281 |
| 8 | 36 | 0.0236 | 36 | 0.0227 | 53 | 0.0245 |
| 9 | 8 | 0.0232 | 63 | 0.0203 | 63 | 0.0244 |
| 10 | 20 | 0.0199 | 39 | 0.0202 | 45 | 0.0222 |
| 11 | 37 | 0.0193 | 10 | 0.0196 | 52 | 0.0202 |
| 12 | 39 | 0.0182 | 2 | 0.0193 | 10 | 0.0195 |
| 13 | 66 | 0.0181 | 8 | 0.0174 | 66 | 0.0176 |
| 14 | 5 | 0.0181 | 67 | 0.0172 | 8 | 0.0172 |
| 15 | 6 | 0.0181 | 53 | 0.0170 | 13 | 0.0170 |

The three methods in TABLE 6 exhibit a consistent ranking of specific nodes. Notably, Node 37 is ranked relatively high in both AHP and AHP-FCM approaches. In terms of data distribution, the variability observed in the data derived from IAHP-FCM is significantly greater, with a variance of 0.1114. This result suggests that IAHP-FCM method is sensitive to the levels of weaknesses among different nodes and so it differentiates in a much better manner. The variances, when measured using AHP by Expert 1 and AHP-FCM were 0.0105 and 0.0698 respectively, which implied homogeneous distribution and lack of sensitivity among node differences. This analysis underlines the necessity and validity of the proposed model.

- Analysis of model sophistication

In this paper, the six nodes with the lowest values from the enhanced node degree index, improved node voltage stability index, traditional AHP analysis, AHP-FCM, and IAHP-FCM are used to validate the accuracy and improvement of IAHP-FCM. The attacks and removal of these nodes are simulated to analyze the stability margin of the power grid. This method is then compared to the random node attack strategy of Liu et al [25]. Normalized results of this comparison are shown in FIGURE 7.

System stability margin variations under different attack modes.

The variations in system stability margins in FIGURE 7 across different attack scenarios provide the following insights:

With the increase in the number of attacked nodes, the stability margin of the power grid declines gradually. Among the five attack modes compared in this paper, the decline in stability margin is the most gradual under the random node attack mode, reflecting the importance of key nodes in the power system. In contrast, the stability margin decreases most quickly under the proposed attack scheme using IAHP-FCM model in this paper, which further demonstrates the effectiveness of the proposed model.

It follows from the analysis that there are significant differences between the node voltage stability index attack mode and the enhanced node degree index when compared under a single metric. Specifically, when targeting the node degree index, the system's stability margin experiences a significantly more pronounced decline following the first and second attacks in comparison to the voltage stability index. However, as the number of compromised nodes escalates, the rate of decline in the system stability margin under the voltage stability index attack mode exceeds that of the node degree index attack mode. This observation underscores the limitations inherent in relying on a single metric for comprehensive assessment.

For random node attacks, as well as for AHP and AHP-FCM methods, there are cases where the stability margin of the system does not practically change after an attack on some nodes. The above phenomenon, however, ensues from very particular features of a ring network, distributed power sources, wherein systems in which nodes that happened to be deemed as 'critical' in a given arrangement, lose most, if not all, relevance owing to a topological feature given by this ring. For example, in the case of the traditional AHP method, after the second attack on Node 4, followed by an attack on Node 11, the system was still in acceptable operation conditions due to the presence of the ring network and DG, and did not show major variations in stability margin. This fact reveals that in that instant of operation, system Node 2 was significantly less vulnerable. Conversely, regarding the attack on IAHP-FCM model, each new attack caused more and more degradation in system stability margin, and hence more reduction in the contribution of ring network and DG to reducing the vulnerability grade of the system nodes. It underlines, as a further confirmation, the efficiency of the scheme proposed.

CONCLUSION

This study proposes IAHP-FCM comprehensive assessment model, based on complex network theory, to effectively identify weak nodes within complex distribution network systems. The proposed model addresses the limitations of single-index approaches by integrating multiple indicators, thereby broadening its applicability and accounting for the interplay of network structure and operational dynamics. Its significant advantages are particularly evident in distribution networks characterized by ring structures and DG.

Through simulation and analysis on IEEE-69 complex active distribution network, the model has demonstrated a notable improvement in the accuracy of weak node identification. These results affirm its potential as a reliable tool for enhancing grid resilience and operational efficiency. However, further research is necessary to address critical challenges, including the nonlinear dynamics introduced by high-penetration distributed energy sources, the cascading impacts of cyber-attacks, and the model's performance under islanded operation scenarios. Exploring the effectiveness of the proposed improvement metrics in these contexts will be crucial. Strengthening the model's capacity to identify and mitigate dynamic disturbances is essential for ensuring the resilience and stability of distribution networks in increasingly complex and variable operational environments.

REFERENCES

- Mahmoodi M ,Abadi R N M S ,Attarha A , et al. Data-driven Distributionally Adjustable Robust Chance-constrained DG Capacity Assessment [J]. Journal of Modern Power Systems and Clean Energy, 2024, 12 (01): 115-127.

- Tianhua Li,Yanchao Du,Yongbo Yuan. Use of Variable Fuzzy Clustering to Quantify the Vulnerability of a Power Grid to Earthquake Damage[J]. Sustainability, 2019, 11: 5633.

- LIU Xiaoming, FENG Zihang, CHEN Hai, et al . Transient Fault Analysis of Short Circuit Faults in DC Distribution Grids with Distributed Generators[J]. Proceedings of the CSU-EPSA, 2024(4):1-10.

- DONG Wu，ZHANG Jian，ZHOU Qinyong, et al. An Overview of the Evolution of Security and Stability of China’s Power System [J/OL]. Electric Power, 2024, http://kns.cnki.net/kcms/detail/11.3265.TM.20240528.1355.004.html.

- WANG Zhe, DUAN Jiali, HE Ping, et al. Exploration on Snow-shaped Grid Structure of Urban Medium Voltage Distribution Network [J/OL] Proceedings of the CSU-EPSA, 2024.https://doi.org/10.19635/j.cnki.csu-epsa.001399.

- XU Yan, SUN Jiling. Multi Fault Repair Strategy for Petal-shape Distribution Network Based on NSGA-Ⅱ [J/OL]. JOURNAL OF ELECTRICAL ENGINEERING, 2024.http://kns.cnki.net/kcms/detail/10.1289.TM.20240724.1347.012.html.

- XU Ze, YANG Wei, ZHANG Wenqiang,et al, Multi-objective distribution network reconfiguration based on chain loops and improved binary particle swarm optimization[J]. Power System Protection and Control, 2021, 49 (06):114-123.

- Wenhao Wang, Yanhui Wang, Guangxing Wang, et al. Identification of the critical accident causative factors in the urban rail transit system by complex network theory[J]. Physica A: Statistical Mechanics and Its Applications, 2023, 610: 128404.

- WU Hui, PENG Minfang, ZHANG Haiyan, et al. Node Vulnerability Assessment for Distribution Network Based on Complex Network Theory[J]. Complex Systems and Complexity Science,2017, 14(01): 38-45.

- Lingen Luo, Bei Han, Marti Rosas-Casals. Network Hierarchy Evolution and System Vulnerability in Power Grids [J]. IEEE SYSTEMS JOURNAL ,2018,12(3),2721-2728.

- XIAO Zhiheng, LIU Huijia. Improved TOPSIS for Node Vulnerability Assessment of Distribution Network Based on Game Theory[J]. Journal of Guangxi Normal University(Natural Science Edition), 2023, 41 (03): 20-30.

- ZHOU Yixi, LI Xiaoming, QU Hezuo, et al. Node integrated vulnerability assessment of complex power grid based on AHP-gray relational degree method[J]. Power System Protection and Control, 2023, 41 (03): 20-30.

- Feng Xiao, Jin Li, Bo Wei. Cascading failure analysis and critical node identification in complex networks [J]. Physica A, 596 (2022) 127117.

- LIU Wenxia, HUANG Yuchen, WAN Haiyang, et al . Application of Complex Network Theory in Vulnerability and Robustness Evaluation of Energy Internet[J]. Smart Power, 2021, 49(01):14-21.

- Radha Ranganathan, Bhuvaneswari Somanathan, Kathiravan Kannan. Fuzzy-Based Cluster Head Amendment (FCHA) Approach to Prolong the Lifetime of Sensor Networks[J]. Wireless Personal Communications, 2019, 110: 1533-1549.

- TANG Xaifei, SUN Rongzuo, TAN Yudong, et al. IED-Attacks Oriented Robust Optimization Model of Defenser-Attacker-Defenser for Multiple Substations[J/OL]. Proceedings of the CSU-EPSA, 2024. https://doi.org/10.19635/j.cnki.csu-epsa.001389.

- LIU Kuan, LIU Haiyuan, ZHANG Lei. An Algorithm for Gene Regulatory Network StructureInference Based on Eigenvector Centrality[J]. Acta Scientiarum Naturalium Universitatis Nankaiensis,,2023,56(4): 40-44.

- CHEN Chao-yang, ZHOU Yong, CHI Ming, et al. Review of large power grid vulnerability based on complex network theory[J]. Control and Decision, 2023, 41(03): 216-220.

- DING Liang, HUANG Jianyang, XU En, et al. Comprehensive vulnerability assessment and structure optimization analysis of power grid  lines considering complex environmental characteristics[J]. Power System Protection and Control, 2021,49(3),105-112.

- MA Qian, WANG Zhaocong, PAN Xueping, et al. Evaluation method of power grid investment decision based onutility function under new electricity reform environment[J]. Electric Power Automation Equipment, 2018,39(12): 198-204.

- JASMON G B, LEE L H C C．Distribution network reduction for voltage stability analysis and load flow calculations[J]. International Journal of Electrical Power and Energy Systems,1991,13(1):9-13.

- WU Xiaomeng, LIU Jian, BI Pengxiang. Research on Voltage Stability of Distribution Networks[J]. Power System Technology, 2006, (24): 31-35.

- MA Li, CHEN Yingyu, TIAN Dingrong, et al. Severity evaluation of multistage voltage sag based on an improved analytic hierarchy process[J]. Power System Protection and Control,2023,51(17): 49-57.

- ZOU Wenbin, HAN Song, RONG Na, et al. Voltage control strategy for a PV inverter based on distributed consensus collaboration[J]. Power System Protection and Control, 2024, 52 (01): 166-173.

- LIU Qingzhen, HUANG Junying, WANG Shaofang. Compounding voltage weakness indicator and reactive power optimization strategy oriented to it[J]. Electric Power Automation Equipment, 2024，44(1): 147-152.

Lingyun Wang received his B.Eng. degree in Electrical Engineering and Automation from China Three Gorges University, China, in 2003, and his Ph.D. degree in Control Science and Engineering from Central South University, China, in 2009. From 2008 to 2009, he participated in a joint doctoral training program and, in 2016, he served as a visiting scholar at Department of Mathematics and Statistics, Curtin University, Australia, from February to August. He is currently a professor at College of Electrical Engineering and New Energy, China Three Gorges University. His research interests include power system operation optimization and control.

Yang Li received his Bachelor's degree in Electrical Engineering and Automation from China Three Gorges University in 2020 and is currently pursuing a Master's degree in Electrical Engineering at the same institution. His research interests include power system operation and control, identification of weak points in distribution networks, and the development and application of graph theory algorithms.

Honglei Xu received the B.Eng., M.Eng., and Ph.D. degrees from Huazhong University of Science and Technology, Wuhan, China, and Curtin University, Perth, WA, Australia, in 1997, 2002, 2005, and 2009, respectively. He is now an associate professor in the School of Electrical Engineering, Computing and Mathematical Sciences, Curtin University. His current research interests include optimization, control and analysis of complex systems with industrial applications, particularly in new energy, mining and construction industry. He acts as an associate editor of the Journal of Industrial and Management Optimization and the Journal of Dynamics of Continuous, Discrete and Impulsive Systems, Series B: Application and Algorithms and an editorial board member or Guest Editor of other six international journals. He acted as stream chair or program member at numerous major international conferences. He is the president of the Australian Society for Operations Research and the president of the Association of Asia-Pacific Operational Research.

Ran Li received her B.Eng. degree in Automation from North China University of Water Resources and Electric Power, China, in 2022. She is currently pursuing an M.Eng. degree in Control Science and Engineering at China Three Gorges University. Her current research interests focus on power equipment fault diagnosis.

Yushan Zhou received her Bachelor's degree in Electrical Engineering and Automation from Foshan University in 2022. She is currently pursuing a Master's degree in Electrical Engineering at China Three Gorges University. Her research interests include power system operation and control, as well as the identification of weak points in power grids.