Analysis of the influence of large-scale offshore wind power on the steady-state voltage of the vicinity region of grid connection point

Weilun Gao 1, Zhigang WU 1*

1 School of Electric Power, South China University of Technology, Guangzhou, China

Correspondence

Weilun Gao, School of Electric Power, South China University of Technology, Guangzhou 510641, China.

Email:641450030@qq.com

Funding information

Science and Technology Project of China Southern Power Grid Corporation,

Grant/Award Numbers: GDKJXM20198236

Abstract: The power characteristics of offshore wind power will change the regional power flow distribution and affect the regional voltage. In this paper, the direct-drive wind turbine generator controlled by unity power factor is selected as the research object, and the influence of change of wind power on voltage at the grid connection point is analyzed from the simple integration model. Based on the two critical states of the external equivalent power of the grid connection point, an analytical expression of the output of wind power in the corresponding state is obtained, and the relationship among the critical state outputs, the output of wind power and the parameters at the grid connection point is drawn, hence the related influence laws is analyzed.  The influence of change of wind power on voltage and regional reactive power and the reactance distribution of transmission lines near the grid connection point is considered to analyze the influence of offshore wind power on the vicinity region of grid connection point. The rationality of the conclusion is verified by study the cases of the integration of offshore wind power into Guangdong power grid, and some suggestions are put forward for the planning of offshore wind power integration.

- Introduction

Compared with onshore wind power, offshore wind power has the advantages of stable wind energy resources, no occupation of land, good consumption conditions and so on. Some countries with long coastlines such as China are rich in offshore wind energy resources, and the development conditions are relatively superior. In recent years, many coastal provinces in China have accelerated the approval and construction of offshore wind power projects, influenced by factors such as technical progress, construction cost reduction and relevant policy supports[1]. The output of offshore wind power is random and fluctuating due to the influence of natural weather conditions, which makes a great impact on the steady power flow distribution of the system when connected to the power grid, and the bus voltage will change with the fluctuation of wind power output, which poses a great challenge to the safe and stable operation of the power grid. It has practical significances to clarify the influence of offshore wind power on the steady-state voltage of grid connection points (GCPs) and the vicinity regions of GCP, analyze the factors affecting the steady-state voltage of GCPs and the influencing mechanism, and put forward the methods to alleviate the risks caused by the uncertainty of wind power.

There are two main aspects to analyze the influence of offshore wind power on the steady-state voltage of the vicinity region of GCP: on the one hand, the influence of wind power on the steady-state voltage distribution of power grid and the voltage stability margin of GCPs are analyzed, on the other hand, the influence of wind power on the static voltage to make a plan for the development of the power grid is considered.

The voltage distribution of each bus in transmission and distribution systems highly depends on the direction of power flow, and the access of distributed generation will directly determine the flow direction, so the randomness of distributed wind turbine output will make the power loss of the transmission line change accordingly. Reference [2-5] study the distribution network model and analyze the influence of distributed wind power on the steady-state voltage of distribution network. In view of the fact that the traditional evaluation method of static voltage stability zone ignores the influence of capacitance parameters, and the stability criterion fails after the d-axis current is saturated, which leads to the large deviation of the evaluation results, an improved characterization method of static voltage stability zone of offshore wind power is proposed in reference [6], which considers the cable capacitance parameters and the saturation effect of converter. In view of the limitation of traditional methods for evaluating the voltage stability area of power grid with offshore wind, which directly regard the wind turbine nodes as PQ nodes and directly connect to the large power grid, a method for evaluating the voltage stability of offshore wind power grid considering the dynamics of cable capacitance and converter is proposed in reference [7]. In order to analyze the impact of intermittent and random output of wind turbines on the power grid, a probabilistic clustering framework is proposed in reference [8], and a wind power model is obtained by implementing four clustering algorithms to evaluate voltage stability. Reference [9] proposes to use sensitive factors to measure the influence of wind turbine groups on the voltage of the GCP under different conditions and expounds the influence of the capacity of wind power, turbine group type, transmission distance, grid structure around the GCP and static var compensator on the voltage of the GCP, by analyzing the voltage fluctuation curve and calculating sensitive factors. Reference [10-13] consider the influence of wind power on the voltage stability of power grid, obtain the P-V curve of  important buses by the Continuation Power Flow (CPF), and analyze the factors affecting the static voltage stability limit of wind power integrated power system. Based on the static voltage stability margin index of power curves of operating transmission lines, a method for evaluating the maximum permeability of wind power under the constraint of static voltage stability is proposed in reference [14]. Because the output range of wind farms is large and the voltage stability will deteriorate with the increase of wind power permeability, reference [15] analyzes the influence of large-scale wind farms on the static voltage stability of power grid by using the P-V curve of Doubly-Fed Induction Generator(DFIG), and analyzes the influence of integrated capacity of wind turbines and power factor on integrated capacity from the perspective of static voltage.

The "source-load" attribute of power system becomes complex and diverse due to the access of new energy, and the power characteristics of nodes in the power system will change. In reference [16], aiming at the steady-state voltage stability in multi-quadrant power mode system, the mechanism of voltage evolution is revealed through the analytical expression and the geometric characteristics of voltage components, and the indices of voltage’s rise and fall are put forward by using normalized voltage sensitivity, which are used to evaluate the safety and stability of steady-state voltage. In order to ensure the safety of large-scale renewable-energy-integrated power system, a data-driven method based on enhanced Gradient Boosting Decision Tree (eGBDT) is proposed in reference [17] for long-term voltage stability evaluation with large-scale high-dimensional PMU measurement. Reference [18] considers the influence of load model on power flow distribution and static voltage stability of power system with wind power integrated.

Considering a series of power quality problems brought to the power grid by the increasing proportion of new energy sources such as wind power and photovoltaic power generation, reference [19-21] analyze the influence of wind power on power grid voltage and put forward reasonable reactive power distribution characteristics to stabilize the influence of wind power on voltage. Reference [22] puts forward an optimization model to determine the maximum capacity of wind farms in power system, which restricts the steady-state security impact of wind turbines on power system by considering various conditions including bus voltage limitation. Reference [23] proposes a conic optimization method based on Semidefinite Relaxation (SDR), which is used to calculate the static voltage stability limit of active distribution network. Considering the uncertainties related to wind speed and load, combined with different wind turbine models, the influence of wind turbines on the evaluation of static voltage stability limit interval is analyzed. Reference [24] considers the influence of location and constant capacity of Distributed Generation (DG) on power loss and voltage stability and proposes a method to site selection and capacity determination of DG suitable for large-scale radial system with the goal of minimizing power loss and improving voltage stability. In reference [25], considering the randomness of wind power output and the influence of energy storage device's ability to stabilize fluctuation on power grid voltage stability, a two-stage stochastic Security Constraint Unit Commitment (SCUC) model considering voltage stability is proposed and solved by Mixed-Integer Nonlinear Program (MINLP). Reference [26] studied the nonlinear influence of uncertainty of new energy output and load output on static voltage stability and proposed a scenario-based scenario construction method to simulate its uncertainty, to obtain customized scenarios for static voltage stability and to avoid the error elimination of extreme scenarios. Reference [27] proposes a global sensitivity analysis method of static voltage stability based on extended affine model, constructs an interval evaluation model of static voltage stability based on L index according to Extended Affine Algorithm, and introduces a global sensitivity analysis method based on variance decomposition to evaluate the importance of input interval variables to static voltage stability.

Some of the above literatures are based on the construction of wind turbine connection model to analyze the influence of various parameters of wind turbine on grid voltage, but the conclusions are not intuitive, and there is a lack of quantitative analysis on the critical conditions of wind power output affecting voltage change of the whole power grid. The PV curve is obtained by CPF to analyze the influence of wind power on the voltage stability margin of power grid, but there is little research on the influence of wind power output change on the voltage in the vicinity region of GCP before the grid reaches the stability limit, although the power system operates in the normal state corresponding to the former for the vast majority of time, the way this state is affected by the grid connection of new energy reflects a deep impact on the voltage stability mechanism. The influence of wind power output fluctuation on GCP voltage is considered in some literatures, but there is no analysis of the influence of wind power output on the voltage around the GCP.

In this paper, the constant power factor control direct-drive wind turbine generator with power factor of 1.0 is taken as the research object, which is a typical practice of modern large power grid such as China Southern Power Grid for direct-drive wind turbine generator in normal steady state. Firstly, based on the analysis of the model of the wind turbine, the influence of the change of wind power on the GCP voltage is concluded. Then, the critical power output value of the wind turbine that changes the GCP voltage state is obtained and the analytical expressions including integrated load, parameters of the wind power integrated transmission line and reactive power compensation of GCP are obtained to analyze the influence of each parameter on the critical power output value of the wind turbine, and further obtain the influence of each parameter on the GCP voltage of the wind turbine. Finally, combined with the change of wind power output and the rule of the variation of GCP voltage, the influence of wind turbines on voltage of the integration area is analyzed, and the rationality of the conclusion is verified by simulating the actual scenarios of Guangdong power grid.

- Simple wind turbine model for analysing the influence of variable wind power output on the voltage stability of GCP

Fig. 2. Schematic diagram of the influence of external equivalent power of GCP on current I

Fig. 1. Grid connection point model of wind turbine

There are two normal control modes of direct-drive wind turbine generator: constant voltage control and constant power factor control. When constant power factor control is selected, the power factor is usually 1.0, which is called unity power factor control. Connect the direct-drive wind turbine generator controlled by unity power factor to the power grid, it only provides active power to the grid in steady state, and there is no exchange of reactive power, as shown in Fig. 1.

In Fig. 1, the influence of unit factor control on the GCP voltage of direct-drive wind turbine generator can be analyzed, where  and  are equivalent electric potential of external power system and the GCP voltage of wind turbine respectively,  is the current flowing from the external power system to the GCP, and  is the reactance value of integrated transmission line of wind turbine. In this paper, it is assumed that the value of resistance is far less than the value of reactance on the transmission line, so the resistance is ignored in the discussion.  is the output active power of the wind turbine, is the amount of reactive power compensation of GCP, and  is the load at GCP.

Combine ,  and  into the external equivalent load  of GCP. That is, , where  is the reactive power loss caused by power flowing through the reactance on the integrated transmission line, then the power generated by external electrical potential source can be expressed as:

where the voltage in the denominator is supposed to be the rated value.

The modulus values on both sides of equation (1) are:

So, the current in Fig. 1 is:

When the wind power  increases from 0, which may cause the external equivalent apparent power of GCP first decreases and then increases. As can be seen in Fig. 2 and equation (3), the current flowing into GCP first decreases and then increases. According to Kirchhoff Voltage Law (KVL), the GCP voltage first increases and then decreases, and with the further increase of wind power output, the GCP voltage will be lower than that before the wind turbine is connected. Based on the above analysis, there will be two critical values of output power of the wind turbine in the process. The first critical value is that makes the GCP voltage change from increasing to decreasing, which is defined as the increasing or decreasing critical output value (IDCOV), and the other critical value is that makes the GCP voltage lower than the voltage value before the wind power is connected, which is defined as the positive and negative critical output value (PNCOV). By discussing the influence of various factors on the two critical values, one can analyze the change of GCP voltage of the corresponding wind farm.

- Calculation of two critical values of wind power

  - Calculation of IDCOV

Based on the model shown in Fig. 1, it can be seen that with the steady-state output  gradually increasing, the reactive power loss  on the integrated transmission line gradually increases, and the external equivalent complex power of GCP changes from  with no wind power output to  with the wind turbine connected. In this process, the external equivalent apparent power of GCP will be minimized with the change of wind power output, hence the IDCOV value should be corresponding to the condition that can minimize the apparent power, according to the analysis in Section 2.

Let , where , and the partial derivative of the steady-state output of the wind turbine can be obtained:

Let equation (4) to be 0, one can get:

where ,

The discriminant of equation (5) is shown in equation (6), which is greater than 0 when the reactive power compensation of the GCP is relatively small:

Therefore, equation (5) has only one real number solution, corresponding to the IDCOV:

  - Calculation of PNCOV

As the wind power output continues to increase, when the external equivalent output value of the GCP is equal to or greater than that before the wind turbine’s connection, according to the analysis in Section 2, the GCP voltage will be lower than the voltage without wind power, so the wind power output value that makes the external equivalent power of the GCP equal before and after the connection is the PNCOV.

Therefore, make the apparent power equal before and after the connection:

Equation (8) can be transformed into

where  , .

The discriminant of equation (9) is shown in equation (10), which is greater than 0 when the reactive power compensation of the GCP is relatively small:

Therefore, equation (9) has only one real number solution, corresponding to the PNCOV:

Based on the above derivation, the analytical expressions of IDCOV and PNCOV can be obtained, which can be used for subsequent analysis. Among them, the greater the IDCOV, the greater the wind power output allowed by the GCP to keep the rising trend of the voltage. The greater the PNCOV, the greater the allowable wind power output value of GCP where the holding voltage is higher than that before the connection. Under the same wind power output, by increasing two critical values, the influence of wind power on the GCP voltage can be improved, and several factors have influence on the two critical output values. By analyzing the influence of those factors, a reasonable optimization scheme of the GCP steady-state voltage can be given.

- Influence of different factors on the two critical values

  - Influence of Active Power of GCP Load P0 on the Two Critical Values

According to equation (5):

Hence the partial derivative of  to IDCOV  is obtained:

Let equation (13) be equal to 0, one can get the  that changes the monotonicity of equation (12):

Since the value of  is small, the second term in equation  will be large, so the critical reactive power compensation value is also large. This means that under the usual reactive power compensation level, the monotonic relationship between and  in equation  can be guaranteed.

Obviously, with the increase of IDCOV ,  increases monotonically. Therefore, when other parameters of the bus remain the same, the larger  before grid connection, the larger IDCOV  it can be. And similarly, there is an identical relationship between  and PNCOV .

  - Influence of reactive power compensation QC at GCP on the two critical values

According to equation (6), when the reactive power compensation  is small enough, the discriminant is greater than 0, and equation (5) has only one real number solution. With the increase of , the discriminant will get smaller until 0. Since  and  become smaller and both are not 0, at this time, two of the three real number solutions of equation (5) are equal, and when the discriminant is less than 0, equation (5) will have three unequal real number solutions. Therefore, the influence of reactive power compensation on the IDCOV  will not be a monotonous function but will be affected by the actual operation parameters and show different fluctuations.

At the same time, equation (10) behaves as:

Fig. 3. Comparison diagram of the relationship between discriminant and reactive power compensation corresponding to equation (6) and equation (10)

According to Fig. 3 and equation (15), with the increase of reactive power compensation , equation (6) will cross the zero value earlier than equation (10), so that the reactive power compensation  value that changes the monotonicity of IDCOV will be smaller than that changes the monotonicity of PNCOV, and with the increase of reactive power compensation , IDCOV will lose monotonicity and fluctuate before PNCOV.

  - Influence of Integrated Transmission Line Parameter X1 on the Two Critical Values

Rewrite equation (5) as

It is obviously that  is greater than 0 under practical conditions. Solving equation (16) one can get:

When  satisfies , the numerator of equation (17) increases monotonically while the denominator decreases monotonically. So, it can be concluded that the larger corresponds to the smaller IDCOV . Similarly, when  meets ,  has the same influence on PNCOV. However, considering that there are both active load and reactive load at GCP, taking PNCOV as an example, which is fulfilled by the external equivalent power of GCP before and after connection, so  is required to be greater than the active load value  of GCP without considering reactive compensation. At this time, with the increase of , the numerator and denominator of equation (17) decrease at the same time, so it is impossible to directly determine the relationship between integrated transmission line parameter  and critical output value, which will be analyzed by simulation results later.

Fig. 4. Model of voltage near GCP

Influence of wind power output on bus voltage near GCP

Fig. 4 shows the model to analyze the voltage near GCP by evaluating the change of voltage  at the position with the distance  from GCP  when  changes, with the voltage difference of GCP before and after the wind turbine is connected to the grid.

According to the analysis in Section 2, during the process of increasing the steady-state output of the wind turbine from 0 to ,  and gradually increases; furthermore, when increasing the steady-state output of the wind turbine from  to ,  and gradually decreases to 0; and finally, when increasing the steady-state output of the wind turbine from  to ,  and its absolute value gradually increases.

According to Fig. 4:

where .

Considering the influence on equivalent load caused by the variation of GCP voltage:

Subtract equation (18) into equation (19):

Let .

When the steady-state output of the wind turbine increases from 0 to IDCOV ,  and gradually

Table 1 Information of selected substations

| Station Name | Active Load in Station P0(MW) | Reactive Load in Station Q0(Mvar) |
| --- | --- | --- |
| YDS21 | 147.9 | 29.6 |
| YPY21 | 194.0 | 39.0 |
| YJP21 | 40.0 | 15.0 |
| YSG21 | 92.0 | 0.0 |

increases, since  remains the same, the reactive power variation  on the integrated transmission line is less than 0 and the absolute value gradually increases. At the same time,  approximately square increases with the steady-state output variation of the wind turbine. Since the value of   increases from 0 and is small at this stage, the voltage  in the area mainly affected by the voltage of GCP gradually increases.

Fig. 5. Relationship between wind power output and GCP voltage

When the steady-state output of the wind turbine increases from IDCOV  to PNCOV ,  but decreases gradually, which makes  less than 0 and the absolute value of  gradually decreases. At the same time,  is approximately square multiplied by the increase of  while  is becoming large in this stage. According to equation (20), the voltage  in the area near GCP decreases with the increase of the wind turbine output, and the influence range gradually increases. However, due to the increase of the wind power output, the active power flow near GCP is satisfied, which reduces the line power flow pressure in the far area, so that the voltage in the area far from the GCP still increases with the increase of the wind turbine output, but the range gradually decreases.

When the steady-state output of the wind turbine increases from PNCOV  to the output limit,  and the absolute value gradually increases,  and  is large than 0 and increases gradually. The change principle is consistent with the process that the steady-state output of the wind turbine increases from IDCOV  to PNCOV , except that the voltage drop area is larger and the increase area is smaller.

- Example analysis

  - Introduction of Example

A series of scenarios based on a typical operation mode of Guangdong power grid is simulated and analyzed in detail, and the direct-drive wind turbine generator controlled by unity power factor is used as the integrated wind turbine type. This power grid is the largest provincial power grid in China, serving one of the most prosperous regions in Chinese economy.

In the base scenario, the number of buses is 13683, the number of branches is 16147, the total generator output is 191293.09MW and the total load is 185971.69MW.

  - Analysis of the Influence of Wind Power on GCP Voltage

Several 220kV substations are randomly selected in the coastal areas of Guangdong Power Grid, which are used to simulate the integration of offshore wind power, and the power output of wind turbines is gradually increased to show the relationship between wind power output and GCP voltage. The information of the selected substations is shown in Table 1.

According to the relationship between the voltage of each station and the wind power output in Fig. 5, it can be seen that although the range of the corresponding curve is different due to the variations of the parameters of each GCP, with the wind power output gradually increasing from 0, the voltage of each GCP shows the same trend of increasing first and then decreasing.

  - Analysis of the Influence of Parameters on the Two Critical Values

YSG21 and YPY21 are selected to analyze, and the influence of each parameter on the two critical output values of wind power is illustrated by the curves of GCP voltage with wind power output under different parameters.

Fig. 6. Relationship between the active GCP load and the voltage of YSG21

Fig. 7. Relationship between the active GCP load and the voltage of YPY21

1)  Influence of active GCP load on the two critical output values

As shown in Fig. 6 and Fig. 7, the thick red curve and the thick blue curve are the curves connected with corresponding IDCOVs and PNCOVs under different load levels, respectively. With the increase of the active GCP load of the grid connection point, the values of IDCOV and PNCOV also increase (see the horizontal coordinate), but the overall change curve shifts downward, and the offset gradually decreases (see the vertical coordinate). Therefore, when the output of the GCP is large, it is necessary to comprehensively consider the two thresholds of the active GCP load.

Fig. 8. Relationship between the GCP reactive power compensation and the voltage of YSG21

Fig. 9. Relationship between the GCP reactive power compensation and the voltage of YPY21

2) Influence of GCP reactive power compensation on the two critical output values

In Fig. 8 and Fig. 9, the thick red curve and the thick blue curve also respectively correspond to the curves connected with IDCOV and PNCOV, now under different GCP reactive power compensation levels, and there is no obvious upward and downward trend of IDCOV and PNCOV (see the horizontal coordinate). At the same time, by comparing the two curves, it can be seen that the monotonicity of IDCOV curve changes while the monotonicity of PNCOV curve remains unchanged during the change of GCP reactive power compensation from 0 to 300MW. On the other hand, the overall curve can be found that with the increase of GCP reactive power compensation, the overall change curve moves upward, and the offset has no obvious change with the increase of wind power steady-state output (see the vertical coordinate). Therefore, more attention should be paid to its variation on the overall voltage curve when considering the change of GCP reactive power compensation.

Fig. 10. Relationship between the reactance of integrated transmission line and the voltage of YSG21

Fig. 11. Relationship between the reactance of integrated transmission line and the voltage of YPY21

3) Influence of integrated transmission line parameter on the two critical values

It can be seen from Fig. 10 and Fig. 11 that the thick red curve and the thick blue curve correspond to the corresponding IDCOV and PNCOV under different reactance changes, and the corresponding IDCOV and PNCOV of the GCP show a decline trend with the increase of the reactance of the integrated transmission line (see the horizontal coordinate), which shows that the two critical output values of the integrated transmission line can be improved by appropriately reducing the reactance value of the integrated transmission line, which can be realized by specific technical measures such as connecting serial reactive power compensation devices in the line. However, the overall change curve shifts downward, and the shift gradually increases with the increase of the steady-state power output of wind power (see the vertical coordinate). Therefore, when the output of wind power is small, it is necessary to consider the comprehensive influence of the reactance of the integrated transmission line on the two critical output values and the overall voltage curve.

Fig. 14. Thermal diagram of voltage change in YSG21 area

Fig. 15. Thermal diagram of voltage change in YPY21 area

SG

Fig. 12. Line Reactance around YSG21

Fig. 13. Line Reactance around YPY21

Analysis of the Influence of Wind Power on Voltages near GCP

The transmission line reactance around YSG21 and YPY21 is shown in Fig. 12 and Fig. 13, respectively. It can be seen that the reactance in the area near YSG21 is obviously greater than that near YPY21, especially in the area near YDL51.

Consider the cases that wind power integrated at YSG21 and YPY21, respectively, and the steady-state power output of wind turbines is increased from 0 to 250MW with a growth rate of 50MW. The voltage changes of GCPs and the buses in the areas near the GCPs are shown in the Fig. 14, Fig. 15 and Table A1, Table A2 in the appendix.

Buses in Fig. 14 and Fig. 15 are sorted from top to bottom according to the transmission line reactance from YSG21 and YPY21, respectively. In order to reflect the change of node voltage more clearly, the voltage values in six scenarios with wind turbine power output of 0MW-250MW are normalized to the node voltage values in the scenario with wind power output of 0MW. The different colors in the figures represent values of their corresponding voltages, and significant change of colors indicates whether the obvious variation of voltage amplitude. The greater the color difference between two adjacent color blocks, the greater the corresponding voltage value changes.

According to the voltage changes of each bus in Table A1 and Fig. 14, it can be seen that the voltage of YSG21 gradually increases with the steady-state output of wind power increasing from 0 to 150MW, and gradually decreases with the steady-state output of wind turbines increasing from 150MW to 250MW. The voltage of buses in the vicinity of YSG21 also follows the trend of increasing first and then decreasing with the steady output of the wind power. However, considering the distance from YSG21 and the difference of line reactance, the voltage changes of each bus are different. Comparing PL, HD and NQ, BL and SF, although they are all near YSG21, the line reactance values of NQ, BL and SF are obviously higher than those of PL and HD. Therefore, after the steady-state output of wind power is more than 100MW, the bus voltage begins to drop. As concluded in section 5, this is because the reactive power flowing through the line reactance is relatively large, and the voltage drop caused by the integrated wind turbine is greater than the voltage promotion effect. This phenomenon is particularly obvious in the vicinity of DL. Because the reactance value of the line near DL is obviously greater than that in other areas, the voltage of the nearby bus even drops immediately.

It can be seen from Table A2 and Fig. 15 that the voltage of YPY21 rises with the steady-state output of wind power increasing from 0 to 150MW, and drops with the steady-state output of wind turbines increasing from 150MW to 250MW, and there is no early voltage drop of buses in its vicinity, which is due to the small reactance value of lines near YPY21 and the small voltage drop caused by reactive power flowing through reactance. At the same time, due to the gradual increase of steady-state output of wind power, the active demand near the GCP is well balanced nearby, which correspondingly reduces the line power flow pressure in the area far from the wind power and makes the voltage of the bus rise in the area far from wind power.

- Conclusion

When the direct-driven offshore wind turbine operated under unity power factor control mode, cases are studied in this paper with the output of the wind turbine gradually increases from 0, and the GCP voltage first increases and then decreases. Several factors have influence on the GCP voltage. With the increase and decrease of the GCP voltage and the change of reactive power of transmission line, the voltage near the grid also changes: when the transmission line reactance near GCP is small, the voltage change trend in this area is mainly affected by the GCP voltage. When the transmission line reactance near GCP is large, the voltage variation trend in this area will also be greatly affected by the change of reactive power demand. For the area far away from GCP, the active power demand in the area near GCP can be better balanced, which reduces the line power flow pressure in the area far away from GCP, so that the voltage in that area may increase compared with the situation where the wind power is not connected to the grid.

Considering of the influence of the above-mentioned large-scale offshore wind power on the GCP voltage and its near area, the following suggestions are put forward when planning of the integration of large-scale offshore wind power is implemented:

1) It is preferable to choose GCP buses with high critical output values.

2) The integrated capacity of the wind turbine should be less than the PNCOV of the GCP.

3) When considering large-scale offshore wind power grid connection, more buses should be selected as far as possible to optimize the influence of wind power on bus voltage of GCP and its near area.

4) The influence of the parameters of GCP on the GCP voltage is related to the steady power output of the wind turbine. When the output is large, different reactance of the grid connection line has a greater influence on GCP voltage, while when the output is small, the change of active GCP load has a greater influence as well.

5) The influence of the change of GCP voltage on regional voltage is related to reactive power loss of wind power integrated transmission lines and reactance of transmission  lines near the GCP. Appropriate shunt and serial reactive power compensation can reduce the influence of wind power on bus voltage near GCP.

This paper mainly focuses on the influence of wind power output change on the voltage of GCP and its near area in typical operation scenarios. However, considering the randomness and fluctuation of wind power itself and the impact of load uncertainty on the load, the power flow of the grid is changing constantly. It is of great significance to discuss the influence of wind power and load change on the power flow distribution in the region near the GCP between similar power flow scenarios, and to stabilize the uncertainty of wind power and load through unit optimization and reasonable distribution of energy storage, which is of great significance to the safe and stable operation of the grid.

AUTHOR CONTRIBUTIONS

Gao Weilun: Investigation, Methodology, Software, Data curation, Formal analysis , Visualization ,Writing – original draft. Wu Zhigang: Funding acquisition, Supervision, Validation, Writing – review & editing.

ACKNOWLEDGEMENTS

This work is supported by science and technology project of China Southern Power Grid Corporation No. GDKJXM20198236, to which the authors are very grateful.

CONFLICTS OF INTEREST

The authors declare that they have no conflicts of interest.

DATA AVAILABILITY STATEMENT

The data that support the findings of this paper are available from the corresponding author upon written official request with a legitimate justification.

ORCID

Gao Weilun: https://orcid.org/0009-0002-6715-834X

PERMISSION TO REPRODUCE MATERIALS

FROM OTHER SOURCES

None

- References

Zhu, L., Zheng, H., Ji, H., et al.: 'Development Trends and Suggestions on Offshore Wind Power of China', 2021 IEEE Sustainable Power and Energy Conference (iSPEC), Nanjing, China, 2021, pp. 2043-2048.

Liu, K., Dong, W., Li, Y., et al.: 'Digital Simulation Analysis of Influence of Distributed Wind Power Generation connected on node voltage of Distribued Network', 2019 14th IEEE Conference on Industrial Electronics and Applications (ICIEA), Xi'an, China, 2019, pp. 1470-1475.

Xu, H. Y.: 'Analysis of Power Flow on Power System with Wind Power Grid', Advanced Materials Research. Trans Tech Publications Ltd, 2014, 860, pp. 275-279.

Tan, H., Li, H., Yao, R., et al.: 'Static voltage stability analysis and evaluation of vector controlled offshore wind farm considering cable capacitance parameters', Frontiers in Energy Research, 2023, 11, pp. 1116090.

Linh, N. T.: 'Voltage stability analysis of grids connected wind generators', 2009 4th IEEE Conference on Industrial Electronics and Applications, Xi'an, China, 2009, pp. 2657-2660.

Tan, H., Li, H., Xiang, X., et al.: 'Characterization of static voltage stability region of offshore wind farms considering submarine cable capacitance parameters and converter saturation', International Journal of Electrical Power & Energy Systems, 2023, 150, pp. 109095.

Alruwaili, M. O., Vaziri, M. Y., Vadhva, S., et al.: 'Impact of distributed generation on voltage profile of radial power systems', 2013 IEEE Green Technologies Conference (GreenTech), Denver, CO, USA, 2013, pp. 473-480.

Rahman, M. T., Hasan, K. N., Sokolowski, P. 'Evaluation of wind farm aggregation using probabilistic clustering algorithms for power system stability assessment', Sustainable Energy, Grids and Networks, 2022, 30, pp. 100678.

Hu, L., Zhang, X., Chang, X., et al.: 'Analysis on contribution of wind power generator groups to voltage fluctuation at point of common coupling', Dianwang Jishu/Power System Technology, 2012, 36, pp. 232-237.

Chen, K., Han, J.: 'Influence of wind power grid connection on static voltage stability', 2020 7th International Forum on Electrical Engineering and Automation (IFEEA), Hefei, China, 2020, pp. 371-374.

Toma, R., Gavrilas, M.: 'Steady state voltage stability study in the context of the integration of a DFIG-based wind farm into the electricity grid', Buletinul Institutului Politehnic Din Iasi Publicat de, 2016, pp. 27-36.

Adetokun, B. B., Muriithi, C. M., Ojo, J. O.: 'Voltage stability assessment and enhancement of power grid with increasing wind energy penetration', International Journal of Electrical Power & Energy Systems, 2020, 120, pp. 105988.

Bhumkittipich, K., Jan-Ngurn, C.: 'Study of voltage stability for 22kv power system connected with lamtakhong wind power plant, Thailand', Energy Procedia, 2013, 34, pp. 951-963.

Tang, Y., Chang, P., Dai, J., et al.: 'Evaluation method of maximum wind penetration level considering static voltage stability constraint', 2020 IEEE International Conference on Power Systems Technology (POWERCON), Bangalore, India, 2020, pp. 1-6.

Jiapaer, A., Zeng, G., Ma, S., et al.: 'Study on capacity of wind power integrated into power grid based on static voltage stability', 2012 IEEE 15th International Conference on Harmonics and Quality of Power, Hong Kong, China, 2012, pp. 855-859.

Zhang, X., Yang, H., Zhou, G., et al.: 'Steady-state voltage stability assessment of new energy power systems with multi-quadrant power modes', Energy Reports, 2023, 9, pp. 3851-3860.

Gao, H., Cai, G., Yang, D., et al.: 'Real-time long-term voltage stability assessment based on eGBDT for large-scale power system with high renewables penetration', Electric Power Systems Research, 2023, 214, pp. 108915.

El-Shimy, M., Mostafa, N., Afandi, A. N., et al.: 'Impact of load models on the static and dynamic performances of integrated wind power plants: A comparative analysis', Mathematics and Computers in Simulation, 2018, 149, pp. 91-108.

Dong, G., Yang, S., Chen, Y., et al.: 'Review on The Influence of New Energy Grid Connection on Power Quality of Power Grid', 2022 7th International Conference on Power and Renewable Energy (ICPRE), Shanghai, China, 2022, pp. 1228-1232.

Zhang, S., Zhang, W., Liu, Q., et al.: 'Study on the Influence of Large-Scale Wind Power Connecting to Power Grid on Voltage Quality Control', Journal of Physics: Conference Series. IOP Publishing, 2019, 1345(5), pp. 052045.

Murthy, P. S., Devaki, P., Devishree, J., et al.: 'A static compensation method based scheme for improvement of power quality in wind generation', 2011 International Conference on Process Automation, Control and Computing, Coimbatore, India, 2011, pp. 1-6.

Zhou, W., Qiu, G. Y., Oodo, S. O., et al.: 'Maximum capacity model of integrated multi-wind farms considering static security constraints in electrical grids', Journal of Physics: Conference Series. IOP Publishing, 2013, 418(1), pp. 012044.

Tong, J., Chang, C., Kaiyao, W.: 'Conic optimization method for voltage stability assessment of active distribution networks with different wind turbine models', International Journal of Electrical Power & Energy Systems, 2022, 142, pp. 108304.

Injeti, S. K., Kumar, N. P.: 'A novel approach to identify optimal access point and capacity of multiple DGs in a small, medium and large scale radial distribution systems', International Journal of Electrical Power & Energy Systems, 2013, 45(1), pp. 142-151.

Ghaljehei, M., Ahmadian, A., Golkar, M. A., et al.: 'Stochastic SCUC considering compressed air energy storage and wind power generation: A techno-economic approach with static voltage stability analysis', International Journal of Electrical Power & Energy Systems, 2018, 100, pp. 489-507.

Wang, C., Wang, L., Deng, X., et al.: 'Scenario-based line switching for enhancing static voltage stability with uncertainty of renewables and loads', International Journal of Electrical Power & Energy Systems, 2023, 145, pp. 108653.

Liao, X., Zhang, M., Le, J., et al.: 'Global sensitivity analysis of static voltage stability based on extended affine model', Electric Power Systems Research, 2022, 208, pp. 107872.

Table A1 Table of bus voltage changes near YSG21

| Output Value of Integrated Wind Turbine /MW Station Name | 0 | 50 | 100 | 150 | 200 | 250 |
| --- | --- | --- | --- | --- | --- | --- |
| LT | 238.58 | 238.63 | 238.66 | 238.65 | 238.62 | 238.57 |
| JS | 237.46 | 237.51 | 237.53 | 237.53 | 237.5 | 237.45 |
| MM | 537.88 | 537.97 | 538.04 | 538.09 | 538.11 | 538.11 |
| LY | 238.49 | 238.54 | 238.56 | 238.56 | 238.53 | 238.47 |
| NW | 237.17 | 237.22 | 237.24 | 237.24 | 237.21 | 237.16 |
| HD | 236.18 | 236.32 | 236.41 | 236.45 | 236.45 | 236.41 |
| PL | 236.04 | 236.18 | 236.26 | 236.31 | 236.31 | 236.27 |
| SG | 236.19 | 236.34 | 236.44 | 236.47 | 236.45 | 236.37 |
| BWFJ1 | 236.19 | 236.34 | 236.4 | 236.4 | 236.32 | 236.16 |
| MMDC2 | 236.43 | 236.53 | 236.59 | 236.61 | 236.6 | 236.55 |
| BL | 235.21 | 235.29 | 235.32 | 235.31 | 235.26 | 235.16 |
| NQ | 235.08 | 235.14 | 235.17 | 235.17 | 235.15 | 235.09 |
| SF | 235.22 | 235.3 | 235.33 | 235.32 | 235.27 | 235.17 |
| DL | 538.72 | 538.71 | 538.69 | 538.66 | 538.61 | 538.56 |
| PD | 234.89 | 234.88 | 234.88 | 234.86 | 234.85 | 234.83 |
| NHJ1 | 231.34 | 231.33 | 231.32 | 231.31 | 231.29 | 231.27 |
| NHJ2 | 234.57 | 234.57 | 234.56 | 234.55 | 234.54 | 234.52 |
| YY | 234.63 | 234.63 | 234.62 | 234.61 | 234.6 | 234.58 |
| YC | 234.6 | 234.59 | 234.59 | 234.58 | 234.57 | 234.55 |
| YCAC | 236.34 | 236.34 | 236.33 | 236.33 | 236.32 | 236.31 |
| SA | 234.76 | 234.75 | 234.74 | 234.73 | 234.71 | 234.69 |
| DG | 234.64 | 234.64 | 234.64 | 234.63 | 234.61 | 234.6 |
| HL | 539.74 | 539.74 | 539.72 | 539.69 | 539.65 | 539.6 |
| HN | 236.47 | 236.47 | 236.46 | 236.46 | 236.44 | 236.43 |
| BH | 234.5 | 234.5 | 234.49 | 234.48 | 234.46 | 234.44 |
| YJ | 234.22 | 234.22 | 234.21 | 234.19 | 234.18 | 234.16 |
| YS | 235.07 | 235.07 | 235.07 | 235.06 | 235.04 | 235.02 |
| MN | 234.68 | 234.68 | 234.68 | 234.67 | 234.65 | 234.63 |
| BJT | 236.08 | 236.08 | 236.07 | 236.06 | 236.05 | 236.04 |
| MH | 233.7 | 233.69 | 233.68 | 233.67 | 233.65 | 233.63 |
| LX | 233.99 | 233.99 | 233.98 | 233.97 | 233.95 | 233.93 |
| DL22 | 234.93 | 234.93 | 234.92 | 234.91 | 234.89 | 234.87 |
| QGL | 234.58 | 234.57 | 234.57 | 234.55 | 234.54 | 234.52 |
| CC | 233.3 | 233.3 | 233.29 | 233.28 | 233.26 | 233.24 |
| YZJ | 232.58 | 232.58 | 232.57 | 232.56 | 232.54 | 232.53 |
| JNDC | 232.6 | 232.59 | 232.59 | 232.57 | 232.56 | 232.54 |

Appendices

Table A2 Table of bus voltage changes near YPY21

| Output Value of Integrated Wind Turbine /MW Station Name | 0 | 50 | 100 | 150 | 200 | 250 |
| --- | --- | --- | --- | --- | --- | --- |
| PT | 225.39 | 225.44 | 225.48 | 225.5 | 225.5 | 225.49 |
| LYG | 225.53 | 225.58 | 225.62 | 225.64 | 225.64 | 225.63 |
| HDI | 225.86 | 225.92 | 225.95 | 225.97 | 225.97 | 225.96 |
| CT | 514.07 | 514.19 | 514.27 | 514.32 | 514.33 | 214.3 |
| NJ | 230.43 | 230.48 | 230.52 | 230.54 | 230.55 | 230.53 |
| JL | 231.73 | 231.8 | 231.84 | 231.86 | 231.86 | 231.84 |
| FS | 231.8 | 231.86 | 231.9 | 231.92 | 231.93 | 231.91 |
| QN1 | 234.0 | 234.06 | 234.09 | 234.11 | 234.12 | 234.11 |
| QN2 | 234.39 | 234.44 | 234.47 | 234.49 | 234.5 | 234.49 |
| ZJ | 234.31 | 234.36 | 234.39 | 234.41 | 234.42 | 234.41 |
| HX | 233.99 | 234.04 | 234.07 | 234.09 | 234.1 | 234.09 |
| SY | 532.82 | 532.95 | 533.07 | 533.16 | 533.25 | 533.31 |
| YF | 234.04 | 234.08 | 234.11 | 234.12 | 234.12 | 234.1 |
| XW | 234.01 | 234.05 | 234.08 | 234.1 | 234.09 | 234.07 |
| ZJ1 | 234.59 | 234.64 | 234.66 | 234.67 | 234.66 | 234.63 |
| WZ | 234.27 | 234.32 | 234.35 | 234.36 | 234.35 | 234.31 |
| BWFJ2 | 233.3 | 233.38 | 233.4 | 233.37 | 233.29 | 233.15 |
| PY | 233.3 | 233.38 | 233.43 | 233.44 | 233.42 | 233.36 |
| TNQYZ | 231.73 | 231.79 | 231.83 | 231.85 | 231.85 | 231.83 |
| FC | 231.89 | 231.95 | 231.99 | 232.01 | 232.01 | 231.98 |
| CG1 | 231.81 | 231.87 | 231.91 | 231.93 | 231.93 | 231.9 |
| HQ | 234.35 | 235.39 | 234.62 | 234.63 | 234.62 | 234.59 |
| ZNC | 234.92 | 234.97 | 235.0 | 235.01 | 235 | 234.97 |
| GN21 | 233.13 | 233.19 | 233.24 | 233.25 | 233.25 | 233.22 |
| GN | 530.87 | 531.01 | 531.14 | 531.25 | 531.34 | 531.4 |
| GN22 | 234.09 | 234.13 | 234.17 | 234.19 | 234.19 | 234.19 |
| RL | 233.97 | 234.01 | 234.04 | 234.06 | 234.07 | 234.07 |
| LYN | 232.04 | 232.11 | 232.17 | 232.21 | 232.23 | 232.24 |
| HDE | 232.07 | 232.14 | 232.2 | 232.24 | 232.26 | 232.27 |
| CS | 232.62 | 232.68 | 232.72 | 232.74 | 232.75 | 232.75 |
| RB | 232.1 | 232.18 | 232.23 | 232.27 | 232.29 | 232.3 |
| YYG | 232.37 | 232.45 | 232.51 | 232.55 | 232.57 | 232.58 |
| WXM1 | 232.09 | 232.16 | 232.22 | 232.26 | 232.28 | 232.29 |
| WXM3 | 232.02 | 232.1 | 232.15 | 232.19 | 232.21 | 232.22 |
| CG2 | 232.04 | 232.11 | 232.17 | 232.21 | 232.23 | 232.24 |
| YCN | 233.39 | 233.45 | 233.48 | 233.49 | 233.48 | 233.45 |