Corresponding Author Summary Profile

Name: Ruifeng Zhao

Gender: Male

Nation: China

Birth: 1981-04-26

Corporation: Power Dispatch and Control Center of Guangdong Power Grid Co., Ltd. Guangzhou, China

Education qualification: Doctor of engineering

Current technical position: Senior engineer

Email: zhaoruifeng@gddd.csg.cn

Interest: power system protection and control

Published papers:

[1]	Zhao Ruifeug, Tan Xonggui, Lu Jiangang,Guo Wenxi, Du Hongwei, A resilientself-healing approach foractive distribution networks consideringdynamic microgrid formation, Energy Science:and Engineering[J],·2024,12(1)·p230-248.

[2]	Zhao Ruifeng, Lu Jiangang, Chen Jinrong, Guo Wenxin, Liang Yongliang, International Journal of Emerging Electric Power Systems[J], 2023, 24(2),·183-192.

[3]	Lu liangang, Lu Junni, Zhao Ruifeng, Chen Fengcha, Wang Qiujie, Yan Wei, A Fast and Accurate·Self-Healing Scheme for Intelligent Distribution Networks Using Mixed Integer LinearProgramming, IEEE Access[J], 2024,12,21586-21595.

[4]	Lu Jiangang , Zhao Ruifeng , Liu Bo , Yu Zhiwen, Zhang Jinjiang, Xu Zhangqiang, An Overview of Non-Intrusive·Load·Monitoring Based on·V-I Trajectory·Signature, Energies[J].2023,16(2),1-15.

[5]	Zhao Ruifeng, Li Shiming, Lu Jiangang, Xu Zhangiang, Chen Zhiwei, Anti Interference Clock· Error Correction· Technology Based on BD3 System, Journal of Physics: Conference Series[C],·2023, 2418(1)

[6]	Lu Jiangang, Zhao Ruifeng, Yu Zhiwen, Dai Yue, Zeng Kaiwen, RL and ahp-basedmulti-Timescalemulti-clock source time synchronization for distribution power internet·of things, Computers, Materials and Continua[J], 2024,78(3),4453-4469

[7]	Zhao Ruifeug, Guo Wenxin, Wang Bin, Pan Zhenning, Li Shiming, Li Bo, Lu Jiangang Gathered grey wolf optimizer based optimal control of doubly-fed induction generator. Power System Protection and Control[J], 2020,48(14),150-158

[8]	Zhao Ruifeng, Lu Jiangang, Liu Bo, Yu Zhiwen, Ren Yanru,·Zheng Wenjle, Non-Intrusive·Load Identification·Method·Based·on Self-Supervised Regularization,·Source:IEEE·Access[J], 2023,11,144696-144704

[9]	Zhao Ruifeng, Lu Jiangang, Guo Wenxin, Zheng Wenjie, Li Shiming, BP-LMS-based BDS-3 power system positioning method, Global Energy·Interconnection[J], 2022, 5(6), p666-674.

A protection scheme based on dual criterion of active injection and virtual voltage for distribution network line with T-connected distributed photovoltaic and load

Junqi Qiu 1, Ruifeng Zhao 2*, Bin Li 1

1 Zhongshan Power Supply Bureau of Guangdong Power Grid Co., Ltd., Zhongshan, China

2 Power Dispatch and Control Center of Guangdong Power Grid Co., Ltd. Guangzhou, China

Abstract: This paper firstly analyses the fault equivalent circuit of DG (Distributed Generation) as a high-frequency harmonic source, and then deduces the fault characteristics of the electrical quantities at both ends on the basis of high-frequency harmonic injection, pointing out the weaknesses: easily affected by the load capacity of the T-connected load. Afterwards, this paper draws the equivalent circuit diagram of the positive sequence component after the fault and derives the difference expression of the virtual electrical quantity at the opposite end under internal or external faults at different locations, and then analyses the fault characteristics of positive sequence under the industrial frequency. On this basis, this paper proposes a double-terminal protection scheme based on the combination of high-frequency harmonic injection and virtual positive sequence differential principle. Finally, the protection scheme is verified on the MATLAB/SIMULINK platform. And the proposed protection method can identify faults within 30ms, with a capability of enduring transient resistance up to 200 Ω, noise immunity reaching 200 dB, and being unaffected by the size of T-connected load capacity or the fault location.

- Introduction

With the depletion of fossil energy and the escalating environmental challenges, the development and utilization of new energy have become imperative to achieve the 'double carbon' goal. In response, China's power grid is strategically shifting its focus towards transforming the energy structure. It is actively fostering a novel power distribution system where renewable clean energy serves as the primary source, and distributed generators (DG) play a crucial role[1-2].

Taking the mainstream inverter technology in distributed power sources as an example, its output characteristics diverge from those of traditional power sources, exhibiting fluctuations, intermittency, and nonlinearity influenced by external factors and control strategies. Consequently, the distribution network undergoes a transformation, shifting from the conventional single-source radial network to a multi-source network post grid connection[3]. Moreover, as the capacity of DG access increases, the grid structure experiences a growing complexity, accompanied by an escalating penetration rate of T-connected DG and T-connected load in the distribution network[4-5].

The increased presence of DG further exacerbates the complexity of fault characteristics in distribution networks, posing significant challenges to existing relay protection systems[6-9]. Ref. [10] emphasizes the importance of signal processing for extracting fault information. Researchers find The Support Vector Machine (SVM) is another well-established method for fault anlysis. And in Ref. [11] introduces a novel protection scheme with a combination of  Wavelet Multi-Resolution Singular Spectrum Entropy and

This work was supported by the Key Science and Technology Project of China Southern Power Grid ：GDKJXM20222496

SVM. Ref. [12] employs DWT for processing three-phase current signals, facilitating the identification and classification of faults. However, these methods face challenges about reliance on high sampling frequencies and so on. Thus, Ref. [13] presents an effective scheme for fault detection using ITD methodology, and the method is not affected by the transition resistance, noise, sampling frequency.

Distribution networks typically employ a three-stage current protection system as their primary defense mechanism. However, the introduction of Distributed Generation (DG) alters short-circuit current levels and distribution paths, leading to a notable reduction in the sensitivity and reliability of current protection. In response, scholars globally have proposed several enhancement schemes based on adaptive algorithms. For instance, Ref. [14] introduces an adaptive current protection tuning method that considers the real-time output influence of upstream DG. In Ref. [15], for downstream DG access scenarios, packets are utilized to adjust real-time protection values for the II and III segments of upper-line current, aiming to enhance sensitivity. The fixed value setting of the adaptive algorithm in high DG access scenarios is, however, relatively complex, requiring verification of its protection performance.

As a commonly used primary protection in the transmission network, double-terminal protection, known for its speed and selectivity, has been introduced into distribution networks containing DG. In Ref. [16], an enhanced double-terminal protection scheme is proposed, leveraging the amplitude of the current at both ends and the equivalent impedance on the outside of the line. Ref. [17] introduces a double-terminal protection scheme for an active distribution network based on the amplitude and phase characteristics of the current's positive sequence fault components at both ends. However, it is important to note that the applicability of the above method is limited to scenarios where DG is connected to the grid through the bus.

For distribution networks with T-connected DG, Ref. [18] proposes a virtual multi-terminal current differential protection scheme based on fault current. Yet, in the presence of a T-connected load branch in the area, there is a susceptibility to trip erroneously during external fault scenarios. As the grid structure of the distribution network becomes increasingly complex, understanding the permeability of the T-connected branch (whether DG or load) is crucial for effective protection.

With the continuous improvement, the applicability of the double-terminal protection scheme still requires refinement, particularly in addressing specific challenges. The advent of power electronic equipment has facilitated the technical implementation of active detection fault identification methods that were originally reliant on additional devices [22], gaining substantial attention in the field. The concept of 'active detection' emphasizes control.

In situations where the power grid faces disturbances, power electronic equipment actively emits characteristic electrical quantities for fault detection. Protection devices form criteria based on differences in injected fault electrical quantities to achieve fault discrimination. Notably, significant research progress has been made in fault detection, location, and reclosing within DC systems [20-21]. However, active detection protection schemes for AC systems with DGs are currently limited to specific scenarios such as islanded microgrids [22-23] and transmission lines of centralized photovoltaic power plants [24]. There is a need for further exploration and application.

In summary, the existing gaps in current researches are: on the one hand, there is no distribution network protection scheme specifically designed for distributed renewable energy sources and loads that are T-connected to the transmission lines. And on the other hand, the control capabilities of distributed renewable energy sources have not been fully utilized to their advantage in distribution network protection, achieving coordination between control and protection.

Therefore, this paper proposes a double-ended double-terminal protection scheme based on the combination of harmonic injection and the virtual electrical quantity difference at the opposite end of the positive sequence network.

This paper begins by briefly outlining the working principle and low-voltage ride-through characteristics of photovoltaic DG based on a voltage source inverter. Subsequently, utilizing harmonic injection, a high-frequency equivalent circuit of the distribution network containing T-connected DG is constructed. The paper analyzes the fault characteristics of harmonic signal currents at both ends in the presence of internal or external faults, unveiling the influence of T-connected load branches on these characteristics and identifying the shortcomings of the proposed scheme. The positive sequence equivalent circuit diagram under industrial frequency is derived, followed by the introduction of a method based on the combination of high-frequency harmonic injection and the virtual positive sequence differential principle. Finally, the effectiveness of the double-terminal differential protection scheme for a distribution network with T-connected DG and load is rigorously verified using MATLAB/SIMULINK, providing valuable insights into its performance and applicability. Accordingly, the main innovations and contributions of the proposed draft are:

①This draft proposes a protection scheme for distribution network lines with T-connected DGs and loads.

②This draft proposes a protection principle based on the idea of coordinated control and protection, combining the control capabilities of distributed renewable energy sources.

③The proposed protection scheme organically integrates two dual-terminal protection criteria, remaining unaffected by power flow direction, type of fault, transition resistance, location of fault, capacity of T-connected load and noise interference, thereby resulting in enhanced reliability.

④The proposed protection scheme has been verified in MATLAB and can achieve fault identification within 30ms. However, it is important to note that the applicability of the above method is limited to scenarios where DG is connected to the grid through the bus.

- High-frequency fault characterization analysis of distribution network with T-connected DG

Fig. 1.  Schematic diagram of the distribution network fault between 12 and 13

With the increasing capacity of Distributed Generation (DG) access, the penetration rate of T-connected DG in the distribution network continues to rise. As depicted in Fig. 1, the distribution network adopts the neutral point non-grounding mode, and DG is T-connected with the MN line. Due to the intervention of the T connection of DG, the differential protection based on electrical quantities at both ends is no longer applicable[21].

The control mode and current output characteristics of DG depend on the degree of Point of Common Coupling (PCC) voltage dip, as outlined below.

Constant Power Mode: In this mode, when operating correctly, Pout=PREF, Qout=QREF (Pout and Qout represent the instantaneous output active power and reactive power of DG, respectively). To decouple P and Q, the d-axis is oriented to the PCC voltage rotation vector (uP,q =0, where uP,q is the q-axis component of instantaneous output active power). In this scenario, the DG current reference value is determined as follows:

(1)

Low-Voltage Ride-Through Mode: In this mode, when the PCC voltage drops abnormally, the DG outputs additional reactive current to provide voltage support. The DG current reference during low-voltage ride-through is determined under the premise of not exceeding the device overload capability, as shown in Eq.2 (assuming the q-axis is 90° ahead of the d-axis). Here, IDGR represents the rated current, uP* is the PCC voltage standard unit value, and K1、K2、Kmax correspond to the voltage support factor, reactive current peak factor, and overload current multiple, respectively.

(2)

Taking into account the unique output control characteristics of DG, this paper proposes a control and protection coordination scheme. The scheme is specifically designed to harmonize with the distinct operational features of DG. Central to this coordination is the utilization of high-frequency harmonic injection, providing an effective approach to ensure the reliable performance and protection of DG within the distribution network.

Fig. 2.  High-frequency equivalent circuit of distribution network fault based on T connection DG injection harmonics

In an ungrounded system, the effects of a phase-to-phase short-circuit fault on the system are more severe, as documented in reference [22]. Protection mechanisms are required to accurately identify and respond to such faults. Therefore, this article focuses on phase-to-phase short circuits.

Taking a three-phase short circuit as an example, Fig.2 illustrates the high-frequency equivalence of the distribution network in the event of a fault, both inside and outside the zone. Here, Distributed Generation (DG) is utilized as the harmonic resource, generating an output current named IH. The protection devices measure harmonic signal currents, IHM and IHN, at two ends of the line, respectively. The positive direction of the current is defined as the line flow to the bus.

Additionally, ZHM and ZHN represent the equivalent harmonic impedance of the upstream system at point M and the equivalent harmonic impedance of the load branch at point N, respectively. ZHL is the equivalent impedance of the T-connected load in the line MN, with its current labelled IHL. The presence of a transition resistance RF, inside and outside the area, introduces a current flow referred to as IF.

It is known from Kirchhoff's law of currents that when a fault happens inside and outside the area, IHM and IHN meet the relationships as defined in Eq.(3). Here, kin and kout represent the modulus ratio of the sum of the high-frequency currents measured by the protection devices on both sides of the MN line to the output current of the harmonic source under faults inside and outside the zone, respectively.

(4)

According to the principle of parallel branch diversion, it is further deduced as shown in Eq.(4) :

(4)

As indicated by Eq.(4), kout is consistently larger than kin when the network parameters are established. The difference between the two is contingent upon the relative magnitudes of impedance parameters, such as ZHL and RF, which will be scrutinized in detail below.

Assuming a harmonic frequency fH of 500 Hz, with ZHM=j30Ω， and ZHN=(40+j40)Ω, the curves of kin and kout are explored under varying transition resistances in the presence of changes in the T-connected load along the line MN in the range of 0~3 MV·A fan (with a power factor of 0.85). The ensuing analysis will provide insights into how the relative magnitudes of impedance parameters and transition resistance influence the relationship between kin and kout, as depicted in Fig. 3.

Fig. 3.  The influence of T-connected load and transition resistance on kin and kout

As depicted in Fig. 3, as the T-connected load increases, both kin and kout exhibit a consistent monotonic downward trend. Moreover, for a given T-connected load, the discrepancy between kin and kout diminishes as the transition resistance increases. This observation implies that under certain conditions, particularly the worst-case scenario, it becomes feasible to identify a dividing line between kin and kout. This serves as the basis for constructing a criterion that can effectively distinguish between internal and external faults in the distribution network.

- Industrial-frequency fault characterization analysis of distribution network with T-connected DG

Fig. 4.  Distribution network topology with internal faults at different locations

The influence of DGs under industrial frequency cannot be ignored, and it is necessary to classify and analyse the internal fault according to different relative positions of the load and DGs. As is shown in Fig.4, the internal faults at Fin1, Fin2, and Fin3 will be analysed below as well as Fout.

Fig. 5.  Feeder fault between M and PCC positive sequence equivalent circuit

When a short circuit fault occurs, the positive sequence equivalent circuit is shown in Fig. 5[23], where ZA1 and ZA2 represent the positive sequence line impedance from M to the fault and from PCC to the fault, respectively. And ZB、 ZC denote the positive sequence line impedance from PCC to the T-connected load and from the T-connected load to N, respectively. In addition, ZS is the system impedance and ZN is the load impedance. ES ,UPCC, UL, UM, UN are positive sequence voltage of voltage source, PCC, T-connected load, M and N respectively. And IM, IN, IF, IL, IDG are positive sequence current flowing through M、N、RF、T-connected load and flowing from DG respectively, for which the positive direction is shown in Fig.5. In this context, the positive direction is illustrated in Fig. 5. It is noteworthy that x is employed to describe the location of the fault point, where x∈ [0,1].

We define that the UN(M) refers to the calculated N-terminal voltage derived by UM and IM. And we have similar definition for UM(N). Then, if there is no fault or the fault occurs outside line MN, for UN(M), we have Eq.(5) as below, where ZA is the positive sequence line impedance from M to PCC. and ZN is the load impedance.

(5)

In the same way, for UM(N), we have a derivation of Eq.6.

(6)

Among them, UM、UN、IM、IN are all measurement results and  IDG、IL can be calculated by UPCC、UL、PREF and ZL.

We define DM(x)、DN(x) as a function of location of the fault as Eq.(7):

(7)

When an internal fault occurs as shown in Fig. 5, Eq.(8) can be inferred from Eq.(5)-(6) as follows, where ZMN is the positive sequence of line MN.

(8)

It can be seen  from Eq.2 that when an internal fault occurs between M and PCC, the voltage of PCC falls down, and the q-axis component of IDG rises as well as the fault voltage. Then we can have Eq.9:

(9)

Further, we have Eq.10 as below, where IF is the positive sequence fault current.

(10)

Because ZA、ZB、ZC are above 0, considering about Eq.9-10, we can have Eq.11:

(11)

And in the same way, when there is a fault between PCC and T-connected load as Fig.6, DN(x) is below as Eq.12, where ZB1 and ZB2 are positive sequence line impedance divided by fault location from PCC to T-connected load.

Fig. 6.  Feeder fault between PCC and T-connected load positive sequence equivalent circuit

(12)

Then, when there is a fault between T-connected load and N as Fig.7, DN(x) is below as Eq.13.

Fig. 7.  Feeder fault between T-connected load and N positive sequence equivalent circuit

(13)

Combined with the analysis of Eq.7-13, it can be seen that the relationship between the characteristic quantity of the fault and the location of the fault x is below as Eq.14.

(14)

We set TM(x) and TN(x) as Eq.15, where TM(x)DM(x)，TN(x)DN(x)。

(15)

From Eq.15 we can know that on x [0.1], TM(x) increases monotonically, while TN(x) decreases monotonically. And there must be a point (x0, TN(x0)) satisfying Eq.16:

(16)

From Eq.16 we can know that T(x0) is not subject to location of DG or T-connected load. Then we can depict DM(x)、 DN(x)、TM(x)、TN(x) on x[0,1] as Fig.8.

Fig. 8.  Image of DM(x)、DN(x)、TM(x)、TN(x)

When a fault occurs anywhere between M and N, DM(x)> T(x0) or DN(x)> T(x0). When a fault occurs outside MN zone, DM(x)= 0 and DN(x)= 0, then DM(x)< T(x0) and DN(x)< T(x0).

As can be seen from the foregoing, the fault current of the DG is determined by the active power reference PREF and PCC positive sequence voltage UPCC. Before the calculation of the fault current of the DG, the UPCC and PREF at the time of the fault must be known. While, the rate of change of primary energy output with time is slow and the occurrence of the obstacle is usually completed in a very short period of time, so that PREF before and after the failure can be approximated as invariant and replaced by PREF from the moment before the failure.

As evident from the preceding information, the fault current of the DG is determined by the active power reference PREF and the positive sequence voltage of the PCC UPCC. To calculate the fault current of the DG, it is crucial to know UPCC and PREF at the time of the fault. However, the rate of change of primary energy output over time is slow, and the occurrence of the obstacle typically takes place in a very brief period. Therefore, PREF before and after the failure can be considered approximately invariant and can be replaced by PREF from the moment just before the failure.

According to the feeder structure shown in Fig.4, the relationship between node voltage and current before the occurrence of a fault is as follows.

(17)

As Eq.17 shows, according to Ohm's law and Kirchhoff's law, we can get UPCC、IDG，and then we can get PREF.

- Design of protection scheme

In order to make the most of the advantages of coordination of control and protection[24], this paper proposes a protection start scheme based on the low-voltage ride-through characteristics of DG as Eq.18, where uPCC is the line voltage at PCC, and ρ is the threshold. In order to ensure a certain margin, ρ in this paper is 90% of the rated voltage at PCC.

(18)

When Eq.18 is satisfied, then the protection starts.

From the analysis in chapter 2, we know that after high-frequency harmonic injection, we can identify internal faults by comparing IKH and IKHset as Eq.19, where IMHx and INHx are harmonic currents measured separately at the M、N terminal. And koutmin is the minimum that can classify external and internal faults. In addition, tset is the time delay margin set to avoid interference with judgment by transient processes after a fault, and the tset is typically 5ms[25].

(19)

The passage indicates that the parameter koutmin, as set, might lead to misjudgments of certain internal faults as external faults, especially in cases involving small-capacity T-connected loads. Furthermore, the relative location between the fault and the T-connected load can influence this judgment. Consequently, additional assessments are deemed necessary, building upon the analysis presented in Chapter 3.

According to Eq.15-17, when the fault occurs outside the zone, DM(x) and DN(x) are both 0 with the ignorance of unbalanced current, and wherever the internal fault occurs, DM(x) and DN(x) are both always above 0.5ZMNIFmin (IFmin is the minimum current in the event of a short circuit at the end of the protection range). So, we can build a new criterion based on this as Eq.20.

(20)

When the relationship between characteristic quantities satisfies Eq. (20), it is identified as an internal fault, and the protective action is maintained. Conversely, if it does not satisfy the equation, it is deemed an external fault or no fault, and the protection remains inactive. The setting value for protection is determined based on the product of the minimum fault current in the event of internal faults and half of the total line impedance. In cases where the fault occurs at the end of the protected line, the characteristic quantity on one side approaches 0, while the quantity on the opposite side is larger than the protection criterion within the interval. This simultaneous use of characteristic quantities on both sides effectively mitigates the dead zone problem at the end of the protection [26].

In accordance with Eq. 19-20, the general criterion is expressed as follows in Eq. (21).

(21)

The protection scheme integrates Cr1 and Cr2 with the time window 5ms for Cr1 (2.5 times the period of a 500Hz signal.), and the time window 20ms for Cr2 (corresponding to a complete power frequency cycle). Furthermore, to mitigate the impact of transient high-frequency responses on the protection criterion after a distribution network fault, a delay of 5ms is required before fault detection. Therefore, the total fault detection time requires: 5ms + 5ms + 20ms = 30ms.

Since the harmonic injection of Cr1 will destroy the extraction of fault features of Cr2, the data extraction of Cr2 is required to precede Cr1. The protection flow chart is below as follows:

Fig. 9.  Protection flow chart

- Simulation verification

In order to verify the effectiveness of the protection scheme proposed in this paper, the 10kV feeder model shown in Fig.4 was established at MATLAB/SIMULINK, and the system and load model parameters are shown in Table 1.

Table 1 Parameters of lines and loads

| Paramrters | Values |
| --- | --- |
| Line impedance per unit length/(Ω·km-1) | 0.25+j0.35 |
| Line length from M to PCC/km | 2.0 |
| Line length from PCC to T-connected load/km | 1.5 |
| Line length from T-connected load to N/km | 1.5 |
| T-connected load impedance/Ω | 10+j5 |
| DG type | PV |
| Rated grid-connected voltage/kV | 10 |
| Rated installed capacity/MW | 1~5 |

In the simulation, the fault occurs at 0.2s, and after a delay of 5ms to measure the electrical quantity of the positive sequence network, the high-frequency injection mode is turned on at 0.225s, where the frequency of the high-frequency current is 500 Hz and the amplitude is 8 percent of the rated current of the line. Fig.10-11 show the current measured at the measurement points on both sides of the M、N under internal and external fault of A-C short circuit. And Fig.12-13 show the 500Hz current measured at the measurement points after harmonic extraction on both sides of the M、N under internal and external fault of A-C short circuit.

Fig. 10.  Image of three-phase currents measured at M、N side under internal fault of A-C short circuit

Fig. 11.  Image of three-phase currents measured at M、N side under external fault of A-C short circuit

Fig. 12.  Image of three-phase 500 Hz currents measured at M、N side under internal fault of A-C short circuit

Fig. 13.  Image of three-phase 500 Hz currents measured at M、N side under external fault of A-C short circuit

Then the fault characteristics of the characteristic quantity proposed in this paper and the feasibility and accuracy of the feeder double-terminal protection method are verified through different fault scenarios, and the fault characteristic quantity and protection action under the conditions of fault inside and outside the line MN, fault operation at the end of the line, etc., are discussed respectively as follows.

  - Different fault types

Table 2 shows the occurrence of different types of faults located between T-connected load and N(transition resistance is 10Ω) in the area.

Table 2 Indicators of Cr1 and Cr2 of different fault types

| Fault types | IKHset | IKH | Dset | DM | DN | Trip |
| --- | --- | --- | --- | --- | --- | --- |
| AG(in) | 10.35 | 8.21 | 0.6 | 1.58 | 0.28 | Y |
| AG(out) |  | 12.55 |  | 0.32 | 0.25 | N |
| BC(in) |  | 6.54 |  | 2.21 | 0.31 | Y |
| BC(out) |  | 13.62 |  | 0.28 | 0.29 | N |
| CG(in) |  | 5.88 |  | 3.09 | 0.33 | Y |
| ACG(out) |  | 13.88 |  | 0.18 | 0.30 | N |
| ABC(in) |  | 2.51 |  | 3.68 | 0.41 | Y |
| ABC(out) |  | 14.32 |  | 0.12 | 0.38 | N |

Table 3 Indicators of conventional differential protection of different fault types

| Fault types | Idset | Id | Trip |
| --- | --- | --- | --- |
| AG(in) | 0.52 | 0.48 | N |
| AG(out) |  | 0.32 | N |
| BC(in) |  | 0.62 | Y |
| BC(out) |  | 0.30 | N |
| CG(in) |  | 0.81 | Y |
| ACG(out) |  | 0.25 | N |
| ABC(in) |  | 1.02 | Y |
| ABC(out) |  | 0.18 | N |

As can be seen from Table 2, different types of faults at the location of Fin3 as Fig.4 depicts with a transition resistance of 10Ω can be effectively identified. In addition, the comparison with the traditional differential protection effect in Table 3 shows that the discrimination effect of single-phase ground faults is poor because the traditional differential protection is greatly affected by the transition resistance[27].

  - Different transition resistors

Considering that the protection judgment under single-phase grounding faults is most susceptible to the influence of transition resistance, the criterion index values of AG fault inside and outside the MN zone under different transition resistances are statistically analysed just as Table 4 shows. The location of fault is between T-connected load and N just as Fin3 (see Fig.4), and the transition resistance is 10Ω.

Table 4 Indicators of Cr1 and Cr2 of different transition resistances

| Transition resistance | IKHset | IKH | Dset | DM | DN | Trip |
| --- | --- | --- | --- | --- | --- | --- |
| 10Ω(in) | 10.35 | 8.21 | 0.6 | 1.58 | 0.28 | Y |
| 10Ω(out) |  | 12.55 |  | 0.32 | 0.25 | N |
| 50Ω(in) |  | 9.54 |  | 1.54 | 0.29 | Y |
| 50Ω(out) |  | 11.88 |  | 0.35 | 0.26 | N |
| 100Ω(in) |  | 10.98 |  | 1.50 | 0.27 | Y |
| 100Ω(out) |  | 10.55 |  | 0.38 | 0.25 | N |
| 200Ω(in) |  | 11.47 |  | 1.41 | 0.28 | Y |
| 200Ω(out) |  | 11.62 |  | 0.41 | 0.28 | N |

From the analysis in Table 4, it can be seen that with the increase of transition resistance, Cr1 is gradually affected and the sensitivity decreases, but DM is less affected by the transition resistance and so combination of Cr1 and Cr2 can still sensitively distinguish faults inside and outside the MN zone.

  - Different fault locations

The next step is to verify whether the location of internal fault will affect the protection judgment. The statistical results are shown in Table 5.

Table 5 Indicators of Cr1 and Cr2 of different fault locations

| Location | IKHset | IKH | Dset | DM | DN | Trip |
| --- | --- | --- | --- | --- | --- | --- |
| Fin1 | 10.35 | 9.88 | 0.6 | 0.55 | 1.71 | Y |
| Fin2 |  | 9.65 |  | 0.72 | 1.29 | Y |
| Fin3 |  | 9.52 |  | 1.58 | 0.28 | Y |
| Fout |  | 12.55 |  | 0.32 | 0.25 | N |

As can be seen from Table 5, the protection criterion proposed in this scheme is not affected by the fault location (the fault location refers to the relative position relationship of the fault point, the T-connection load and the DG, as shown in Fig.4)

  - Different T-connected load capacities

Table 6 Indicators of Cr1 and Cr2 of different T-connected load capacities

| Load power multiple | IKHset | IKH | Dset | DM | DN | Trip |
| --- | --- | --- | --- | --- | --- | --- |
| 0(in) | 10.35 | 6.18 | 0.6 | 1.81 | 0.28 | Y |
| 0(out) |  | 15.65 |  | 0.35 | 0.27 | N |
| 1.0(in) |  | 8.21 |  | 1.58 | 0.28 | Y |
| 1.0(out) |  | 12.55 |  | 0.32 | 0.25 | N |
| 1.2(in) |  | 9.82 |  | 1.20 | 0.32 | Y |
| 1.2(out) |  | 11.53 |  | 0.38 | 0.29 | N |
| 1.5(in) |  | 10.86 |  | 1.12 | 0.35 | Y |
| 1.5(out) |  | 10.89 |  | 0.43 | 0.31 | N |

It can be seen from Table 6 that under different T-connected load capacities, it becomes difficult for Cr1 to distinguish faults inside and outside MN zone with the increase of T-connected load capacity, but Cr2 can still maintain good sensitivity, so the protection criterion of the proposed scheme in this paper can not be affected by the T-connected load capacity by combining Cr1 and Cr2.

  - Different Noise

Table 7 Indicators of Cr1 and Cr2 of different noise

| Noise | IKHset | IKH | Dset | DM | DN | Trip |
| --- | --- | --- | --- | --- | --- | --- |
| 10dB(in) | 10.35 | 8.21 | 0.6 | 1.58 | 0.28 | Y |
| 10dB(out) |  | 12.55 |  | 0.32 | 0.25 | N |
| 50dB(in) |  | 9.12 |  | 1.53 | 0.31 | Y |
| 50dB(out) |  | 11.32 |  | 0.32 | 0.28 | N |
| 100dB(in) |  | 8.98 |  | 1.46 | 0.27 | Y |
| 100dB(out) |  | 12.95 |  | 0.39 | 0.26 | N |
| 200dB(in) |  | 9.12 |  | 1.52 | 0.30 | Y |
| 200dB(out) |  | 11.88 |  | 0.44 | 0.38 | N |

It can be seen that the proposed protection scheme has a certain degree of noise resilience, effectively resisting moderate to high levels of noise, though not likely to withstand extremely loud noises such as those approaching 200 dB.

- Conclusion

This paper introduces a protection method that combines high-frequency harmonic injection with the virtual positive sequence differential principle. The effectiveness of the proposed protection scheme is validated through MATLAB/SIMULINK simulation, leading to the following conclusions:

1)The distinction between internal faults and external faults remains unaffected by fault type, location, transition resistance, noise and T-connected load capacity in this protection scheme.

2)The proposed protection scheme seamlessly integrates injection and positive sequence network methods, leveraging the advantages of coordinated control and protection. This approach optimally exploits the characteristics of DG.

3)In comparison to traditional differential protection schemes, the proposed method eliminates protection dead zones and remains unaffected by transition resistance, making it particularly well-suited for distribution lines with T-connected DG and load.

- References

- A. Ibrahim and M. J. Hossain.:‘Low Voltage Distribution Networks Modeling and Unbalanced (Optimal) Power Flow: A Comprehensive Review’, IEEE Access. 2021, 9 , pp. 143026-143084

- V. L. Srinivas, B. Singh and S. Mishra.:‘Fault Ride-Through Strategy for Two-Stage Grid-Connected Photovoltaic System Enabling Load Compensation Capabilities’, IEEE Transactions on Industrial Electronics. 2019, 66, pp. 8913-8924

- X. Zheng, et al.:‘High-Frequency Fault Analysis-Based Pilot Protection Scheme for a Distribution Network With High Photovoltaic Penetration’, IEEE Transactions on Smart Grid. 2023, 14, pp. 302-314

- L. Zhang, et al.:‘Multi-Layer Fault-Tolerant Protection Strategies for Hybrid Distribution Transformers Integrated Photovoltaic Systems’, IEEE Transactions on Industry Applications. 2023, 59, pp. 3098-3109

- Y. Wang, G. Wei, H. Yang, et al.:‘Novel Protection Scheme of Single-Phase Earth Fault for Radial Distribution Systems With Distributed Generators’, IEEE Transactions on Power Delivery. 2018, 33, pp. 541-548

- M. N. Alam, S. Chakrabarti and A. K. Pradhan.:‘Protection of Networked Microgrids Using Relays With Multiple Setting Groups’, IEEE Transactions on Industrial Informatics.vol. 2022, 18, pp. 3713-3723

- E. Ghiani, R. Di Gregorio and S. Hoppert.:‘Planning and Operation of an Intelligent Power Electronics Series Voltage Regulator for PV-Rich Distribution Feeders’, IEEE Open Access Journal of Power and Energy. 2023, 10, pp. 363-372

- B. Han, H. Li, G. Wang, et al.:‘A Virtual Multi-Terminal Current Differential Protection Scheme for Distribution Networks With Inverter-Interfaced Distributed Generators’, IEEE Transactions on Smart Grid. 2018, 9, pp. 5418-5431

- S. Shen, et al.: ‘Regional Area Protection Scheme for Modern Distribution System’, IEEE Transactions on Smart Grid. 2019, 10, pp. 5416-5426

- M.A. Aftab, SS.Hussain, l. All, et al.: Dynamic protecuon or power systemswith high penetration of renewables: a review of the traveling wave based faultlocation techniques, Int. J. Electr. Power Energy Syst. 2020. 114. 105410

- Tang, L. Mahela, O.P, et al.: Current- and Voltage-Actuated Transmission Line Protection Scheme Using a Hybrid Combination of Signal Processing Techniques. Sustainability. 2023. 15. 5715

- Swetapadma, A., Yadav, A. & Abdelaziz, A.Y.: Intelligent schemes for fault classification in mutually coupled series-compensated parallel transmission lines. Neural Comput & Applic. 2020. 32. pp. 6939–6956

- A. Jodaei a , Z. Moravej a , M. Pazoki.: ‘Effective protection scheme for transmission lines connected to large scale photovoltaic power plants’, Electric Power Systems Research. 2024. 228. 110103

- M. Kavi, Y. Mishra and M. Vilathgamuwa.:‘Morphological Fault Detector for Adaptive Overcurrent Protection in Distribution Networks With Increasing Photovoltaic Penetration’, IEEE Transactions on Sustainable Energy. 2018, 9, pp. 1021-1029

- S. Biswal and S. R. Samantaray.:‘An Effective Protection Coordination Scheme for Networked Microgrids Based on Nonstandard Tripping Characteristics of DOCRs’, IEEE Systems Journal. 2023, 17, pp. 6588-6599

- Y. Ueda, K. Kurokawa, T. Tanabe et al.:‘Analysis Results of Output Power Loss Due to the Grid Voltage Rise in Grid-Connected Photovoltaic Power Generation Systems’, IEEE Transactions on Industrial Electronics. 2008, 55, pp. 2744-2751

- F. Alasali, et al.:‘Advanced Coordination Method for Overcurrent Protection Relays Using New Hybrid and Dynamic Tripping Characteristics for Microgrid’, IEEE Access. 2022, 10, pp. 127377-127396

- T. S. Ustun and Y. Aoto.:‘Analysis of Smart Inverter’s Impact on the Distribution Network Operation’, IEEE Access. 2019, 7, pp. 9790-9804

- M. A. Ismeil, A. Alfouly, H. S. Hussein et al.:‘Hardware in the Loop Real-Time Simulation of Improving Hosting Capacity in Photovoltaic Systems Distribution Grid With Passive Filtering Using OPAL-RT’, IEEE Access. 2023, 11, pp. 78119-78134

- D. Zhang, J. Li and D. Hui.:‘Coordinated Control for Voltage Regulation of Distribution Network Voltage Regulation by Distributed Energy Storage Systems’, Protection and Control of Modern Power Systems. 2018, 3, pp. 1-8

- Y. Jiang, F. Mei, J. Lu et al.:‘Two-Stage Joint Optimal Scheduling of a Distribution Network With Integrated Energy Systems’, IEEE Access. 2021, 9, pp. 12555-12566

- M. Shaik, S. K. Yadav and A. G. Shaik.:‘An EMD and Decision Tree-Based Protection Algorithm for the Solar PV Integrated Radial Distribution System’, IEEE Transactions on Industry Applications. 2021, 57, pp. 2168-2177

- B. -L. Zhang, M. -F. Guo, Z. -Y. Zheng, et al.:‘Fault Current Limitation With Energy Recovery Based on Power Electronics in Hybrid AC–DC Active Distribution Networks’, IEEE Transactions on Power Electronics. 2023, 38, pp. 12593-12606

- M. Manohar, E. Koley and S. Ghosh.:‘Stochastic Weather Modeling-Based Protection Scheme for Hybrid PV–Wind System With Immunity Against Solar Irradiance and Wind Speed’, IEEE Systems Journal 2020. 14.  pp. 3430-3439

- X. Diao, et al.: ‘A New Efficient Bidirectional T-Source Circuit Breaker for Flexible DC Distribution Networks’, IEEE Journal of Emerging and Selected Topics in Power Electronics. 2021, 9, pp. 7056-7065

- K. Jia, C. Gu, Z. Xuan, et al.:‘Fault Characteristics Analysis and Line Protection Design Within a Large-Scale Photovoltaic Power Plant’,  IEEE Transactions on Smart Grid. 2018, 9, pp. 4099-4108

- H. R. Baghaee, D. Mlakić, S. Nikolovski, et al.:‘Support Vector Machine-Based Islanding and Grid Fault Detection in Active Distribution Networks’, IEEE Journal of Emerging and Selected Topics in Power Electronics. 2020, 8, pp. 2385-2403

- M. Bhatnagar, A. Yadav and A. Swetapadma.:‘A Resilient Protection Scheme for Common Shunt Fault and High Impedance Fault in Distribution Lines Using Wavelet Transform’, IEEE Systems Journal, 2022, 4, pp. 5281-5292

- D. R. R. Penido, L. R. de Araujo, V. T. S. Rodrigues et al.:‘An Analytical Zero Sequence Method to Locate Fault in Distribution Systems Rich in DG’, IEEE Transactions on Smart Grid. 2022, 13, pp. 1849-1859

- H. R. Baghaee, D. Mlakić, S. Nikolovski, et al.:‘Anti-Islanding Protection of PV-Based Microgrids Consisting of PHEVs Using SVMs’, IEEE Transactions on Smart Grid. 2020, 11, pp. 483-500

- M. -T. Kuo and W. -Y. Lo.:‘A Combination of Concentrator Photovoltaics and Water Cooling System to Improve Solar Energy Utilization’, IEEE Transactions on Industry Applications. 2014, 50, pp. 2818-2827