Mutual inductance parameter measurement and experimental research of double circuit based on different frequency method

Zeyang Lei1,2、Xiaojun Zhang*1,2，Wenbing Zhuang 1,2，Wei Liu1,2，Suzhou Wu1,2，Siyi Qi1,2

- State Grid Xinjiang Electric Power Research Institute Urumqi, Xinjiang, 830011; 2. Key Laboratory of Extreme Environmental Operation and Testing Technology for Transmission and Transformation Equipment in Xinjiang, 830011)

Abstract

In order to improve the measurement accuracy of mutual inductance parameters of transmission lines in the environment of double circuit power lines without power outage, this paper establishes simulation models for measuring mutual inductance parameters of transmission lines using the different frequency method in two modes: equal and unequal zero sequence self-parameters of two circuit lines, using a parallel zero sequence coupling model of double circuit power lines. In the article, simulation analysis is conducted on the line parameters with a coupling coefficient between 0.4 and 0.6 and a line length of 20km-50km.In order to further verify the correctness of the simulation model and measurement methods, a test bench was established based on the principle of line mutual inductance parameter testing in a laboratory dual circuit line without power outage environment for experimental testing. By comparing the test values under experimental conditions with the standard values, it has been proven that the model and method can meet the actual measurement requirements of engineering.

Key words

different frequency method, line parameters, simulation model, double circuit

- 1 INTRODUCTION

With the rapid development of power network construction, transmission lines, as the carrier of power transmission are becoming more and more dense. This leads to the inevitable problem of electromagnetic coupling and interference between the lines [1,2]. And the accuracy measurement of transmission line parameters plays an important role in relay protection setting, line short-circuit calculation analysis, line fault measurement and judgment, etc. It guarantees the stability and safety of power system operation [3,4].

When measuring line parameters, the line to be measured will generate induced current and voltage due to the electromagnetic coupling between the transmission lines. It has a great impact on the accurate acquisition of line parameters, so many domestic and foreign scholars have carried out corresponding research on line parameter testing methods. Currently can be divided into (1) The lumped parameter model or time-varying dynamic phasor model is used to establish an equation between the line parameters and the measured data to solve the line parameter values [5,6]. (2) The power outage measurement method or band point measurement method in the field measurement method is used. Chen Taishou et al. used the combination of global Positioning System (GPS) technology and live line measurement method to measure and compare the parameters of transmission lines in high altitude areas [7]. Ruan Wenkai et al. combined the distributed parameter model with the single-ended measurement method. They carried out theoretical analysis and simulation research on zero-sequence parameters of double circuit transmission lines to solve the drawbacks of traditional single-ended measurement [8]. The single-end measurement method in the state of outage is generally only applicable to the newly built power network and the state of power maintenance. However, the on-line measurement method based on wide area measurement system WAMS [9,10] generally adopts the tripping action of reclosing device to obtain zero sequence parameters, which disturbs the stability of the power system. (3) In order to solve the electromagnetic coupling interference during line parameter measurement, power frequency anti-interference method and different frequency anti-interference method are adopted [11]. The power frequency anti-interference method can be divided into reverse polarity method, increment method, large current method and increment method. The anti-interference method of different frequency can be divided into sweep frequency method, harmonic method and different frequency method, which combine sweep frequency measurement and fitting curve. Based on the measurement principle of zero-sequence impedance parameters, Hu Zhijian et al. used incremental method, different frequency method, high current method, phase reversal method and interference method to conduct simulation and comparative analysis of zero-sequence impedance parameters of lines [12].

In this paper, the simulation model of mutual inductance parameter measurement of double circuit in non-outage environment is established. The different frequency method is used to simulate the parameters of double circuit with equal zero sequence self-parameters and double circuit with unequal zero sequence self-parameters. At the same time, the test bench of mutual inductance parameters under the double-circuit incomplete stop mode is set up in the laboratory environment. The test data were collected for comparison and verification.

2 Measurement Model and Simulation of Mutual Inductance Parameters for Double Circuit Transmission Lines

2.1 Establishment of measurement model for mutual inductance parameters of double circuit

Different frequency method adopts different frequency power supply instead of power frequency power supply as test power supply to avoid power frequency interference in the measurement process. First, the voltage and current of the measured signal are extracted, and then the impedance of the zero sequence is calculated. After frequency conversion, the power frequency zero sequence impedance of the line is obtained.

FIGURE 1 Zero sequence coupling model of parallel lines

The zero-sequence coupling model of parallel transmission lines shown in Figure 1 can obtain the volt-ampere characteristics, which can be expressed by the following equations.

(1)

Where I10=I1+I1p2、I20=I2+I2p2、U10=U1-U1p and U20=U2-U2p. All electrical quantities are zero sequence phasors.

In order to reduce the error caused by capacitive current, this paper adopts the interference method of averaging the current phasor at the head and end. Considering that the mutual inductance parameters of the double-circuit line are tested in the field without power outage, the double circuit tested are generally parallel to the same tower. Therefore, it is divided into two lines zero sequence self-parameters equal (Z11=Z22) and two lines zero sequence self-parameters unequal (Z11≠Z22).

2.2 Simulation analysis based on zero sequence self-parameter equality of double circuit

When the zero sequence self-parameters of two circuit lines are equal (Z11=Z22), there are only two unknown variables. Therefore, only the electrical quantities of two lines under one operational condition are needed to calculate the values of Z11, Z12, and Z22. Based on this operating condition, a simulation model can be established as shown in Figure 2, where the zero sequence self-parameters are equal.

FIGURE 2 Simulation model with zero sequence self-parameter equality

As shown in Figure 2, the solution formula of different frequency impedance parameters is as follows

(2)

(3)

Where, I1=I11+I11p2 and I2=I12+I12p2. All electrical quantities are a different frequency zero sequence phasor.

The different frequency zero sequence impedance is converted to the power frequency zero sequence impedance as follows:

(4)

Where, f0=50Hz. In this paper, the frequency of two different frequency test power supplies is f1=45 Hz and f2=55Hz.

According to the simulation model when the zero sequence self-parameters are equal, as shown in Figure 2, the states with the line length of 20km, 35km and 50km are discussed respectively. (1) Set the transmission line zero sequence impedance Z11=0.208Ω+j1.018Ω/km and when the mutual inductance coefficient K=0.4, the zero sequence mutual impedance between line 1 and line 2 is Z12=0.172Ω+j0.408Ω/km. (2) Set the transmission line zero sequence impedance Z11=0.2366Ω+j1.0757Ω/km and when the mutual inductance coefficient K=0.5, the zero sequence mutual impedance between line 1 and line 2 is Z12=0.2013Ω+j0.5384Ω/km. (3) Set the transmission line zero sequence impedance Z11=0.2389Ω+j1.0853Ω/km and when the mutual inductance coefficient K=0.6, the zero sequence mutual impedance between line 1 and line 2 is Z12=0.2044Ω+j0.6455Ω/km. The measurement results of zero sequence impedance of different frequency test power supply with frequency f1=45 Hz and f2=55Hz can be obtained by simulation. By converting the measured cross-frequency impedance to the power frequency of 50Hz, the parameter values and errors of double-circuit lines of different lengths can be obtained when the zero-sequence self-parameters of the double circuit are equal (Z11=Z22) as shown in Table 2.

TABLE 1 Parameter Values and Errors of Two Circuit Lines with Equal Zero Sequence Self Parameters (Z11=Z22)

| Parameter values and errors of double circuit lines with different lengths when mutual inductance is K=0.5 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| title | R11 | X11 | R22 | X22 | R12 | X12 |
| The measured value of L1=20km (Ω/km) | 0.2082 | 1.0188 | 0.2082 | 1.0188 | 0.1716 | 0.4084 |
| The parameter errors of L1=20km (%) | 0.1191 | 0.0670 | 0.1191 | 0.0670 | 0.4403 | 0.1479 |
| The measured value of L2=35km (Ω/km) | 0.2082 | 1.0188 | 0.2082 | 1.0188 | 0.1720 | 0.4083 |
| The parameter errors of L2=35km (%) | 0.1030 | 0.0687 | 0.1030 | 0.0687 | 0.2280 | 0.1439 |
| The measured value of L3=50km (Ω/km) | 0.2074 | 1.0185 | 0.2074 | 1.0185 | 0.1714 | 0.4080 |
| The parameter errors of L3=50km (%) | 0.2481 | 0.0375 | 0.2481 | 0.0375 | 0.5674 | 0.0540 |
| Parameter values and errors of double circuit lines with different lengths when mutual inductance is K=0.5 |  |  |  |  |  |  |
| title | R11 | X11 | R22 | X22 | R12 | X12 |
| The measured value of L1=20km (Ω/km) | 0.2390 | 1.0739 | 0.2390 | 1.0739 | 0.2029 | 0.5366 |
| The parameter errors of L1=20km (%) | 0.9988 | 0.1677 | 0.9988 | 0.1677 | 0.7943 | 0.3389 |
| The measured value of L2=35km (Ω/km) | 0.2390 | 1.0752 | 0.2390 | 1.0752 | 0.2032 | 0.5378 |
| The parameter errors of L2=35km (%) | 0.9847 | 0.0493 | 0.9847 | 0.0493 | 0.9613 | 0.1163 |
| The measured value of L3=50km (Ω/km) | 0.2383 | 1.0748 | 0.2383 | 1.0748 | 0.2026 | 0.5373 |
| The parameter errors of L3=50km (%) | 0.6825 | 0.0916 | 0.6825 | 0.0916 | 0.6463 | 0.2100 |
| Parameter values and errors of double circuit lines with different lengths when mutual inductance is K=0.6 |  |  |  |  |  |  |
| title | R11 | X11 | R22 | X22 | R12 | X12 |
| The measured value of L1=20km (Ω/km) | 0.2406 | 1.0848 | 0.2406 | 1.0848 | 0.2055 | 0.6448 |
| The parameter errors of L1=20km (%) | 0.6857 | 0.0545 | 0.6857 | 0.0545 | 0.5095 | 0.1072 |
| The measured value of L2=35km (Ω/km) | 0.2402 | 1.0850 | 0.2402 | 1.0850 | 0.2054 | 0.6450 |
| The parameter errors of L2=35km (%) | 0.5071 | 0.0355 | 0.5071 | 0.0355 | 0.4481 | 0.0805 |
| The measured value of L3=50km (Ω/km) | 0.2402 | 1.0856 | 0.2402 | 1.0856 | 0.2054 | 0.6455 |
| The parameter errors of L3=50km (%) | 0.5132 | 0.0158 | 0.5132 | 0.0158 | 0.4799 | 0.0003 |

2.3 Simulation analysis based on zero sequence self-parameters inequality of double circuit

When the zero sequence self-parameters of the double circuit are not equal (Z11≠Z22), there are three unknown variables. So, knowing the electrical quantities of the double circuit in two independent modes of operation can get Z11, Z22, and Z12. Figure 3 shows the simulation model of independent operation mode 1 with unequal zero-sequence self-parameters. The line 1 has a power outage, with a high-frequency power supply added at the beginning and a three-phase short circuit grounded at the end. The line 2 operates normally with power on. Figure 4 shows the simulation model of independent operation mode 2 with unequal zero-sequence self-parameters. The line 1 operates normally with power on. The line 2 has a power outage, with a high-frequency power supply added at the beginning and a three-phase short circuit grounded at the end.

FIGURE 3 Simulation model for independent operation mode 1 with unequal zero-sequence self-parameters

FIGURE 4 Simulation model for independent operation mode 2 with unequal zero sequence self-parameters

Zero-sequence impedances of different frequencies can be obtained from the simulation models of two independent operating modes as shown in FIGURE 3 and FIGURE 4:

Z11=I120U21-I220U11I120I210-I110I220         (5)

Z12=U11I120-I110I120Z11          (6)

Z22=U12I120-I110I120Z12            (7)

Where,I110=I12+I12p2,I120=I12+I12p2,I210=I21+I21p2 and I220=I22+I22p2. All electrical quantities are heterofrequency zero sequence phasor.

Through simulation, the measurement results of zero sequence impedance of different frequency test power supply at different frequency f1=45 Hz and f2=55Hz can be obtained. The measured different frequency impedance is converted to the power frequency 50Hz. The parameter values and errors of double circuit lines of different lengths can be obtained when the zero sequence self-parameters of double-circuit lines are not equal (Z11≠Z22), as shown in Table 2.

TABLE 2 Parameter Values and Errors of Double Circuit Lines with Unequal Zero Sequence Self Parameters (Z11 ≠ Z22)

| Parameter values and errors of double circuit lines with different lengths when mutual inductance is K=0.4 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| title | R11 | X11 |  |  | R22 | X22 |  |  | R12 | X12 |
| The measured value of L1=20km (Ω/km) | 0.2086 | 1.0183 |  |  | 0.2237 | 1.0155 |  |  | 0.1721 | 0.4079 |
| The parameter errors of L1=20km (%) | 0.3222 | 0.0212 |  |  | 0.2174 | 0.0431 |  |  | 0.1664 | 0.0365 |
| The measured value of L2=35km (Ω/km) | 0.2086 | 1.0184 |  |  | 0.2237 | 1.0156 |  |  | 0.1724 | 0.4080 |
| The parameter errors of L2=35km (%) | 0.3111 | 0.0313 |  |  | 0.2302 | 0.0468 |  |  | 0.0066 | 0.0617 |
| The measured value of L3=50km (Ω/km) | 0.2083 | 1.0186 |  |  | 0.2234 | 1.0157 |  |  | 0.1722 | 0.4081 |
| The parameter errors of L3=50km (%) | 0.1712 | 0.0502 |  |  | 0.0993 | 0.0634 |  |  | 0.0686 | 0.0819 |
| Parameter values and errors of double circuit lines with different lengths when mutual inductance is K=0.5 |  |  |  |  |  |  |  |  |  |  |  |
| title | R11 | X11 |  |  | R22 | X22 |  |  | R12 | X12 |
| The measured value of L1=20km (Ω/km) | 0.2372 | 1.0745 |  |  | 0.2523 | 1.0716 |  |  | 0.2010 | 0.5372 |
| The parameter errors of L1=20km (%) | 0.2338 | 0.1115 |  |  | 0.1469 | 0.1072 |  |  | 0.1436 | 0.2169 |
| The measured value of L2=35km (Ω/km) | 0.2372 | 1.0756 |  |  | 0.2523 | 1.0727 |  |  | 0.2013 | 0.5382 |
| The parameter errors of L2=35km (%) | 0.2102 | 0.0151 |  |  | 0.1606 | 0.0067 |  |  | 0.0061 | 0.0327 |
| The measured value of L3=50km (Ω/km) | 0.2369 | 1.0758 |  |  | 0.2521 | 1.0729 |  |  | 0.2011 | 0.5383 |
| The parameter errors of L3=50km (%) | 0.1107 | 0.0053 |  |  | 0.0676 | 0.0138 |  |  | 0.0759 | 0.0094 |
| Parameter values and errors of double circuit lines with different lengths when mutual inductance is K=0.6 |  |  |  |  |  |  |  |  |  |  |
| title | R11 | X11 |  |  | R22 | X22 |  |  | R12 | X12 |
| The measured value of L1=20km (Ω/km) | 0.2399 | 1.0851 |  |  | 0.2550 | 1.0822 |  |  | 0.2046 | 0.6452 |
| The parameter errors of L1=20km (%) | 0.3698 | 0.0242 |  |  | 0.2967 | 0.0174 |  |  | 0.0960 | 0.0507 |
| The measured value of L2=35km (Ω/km) | 0.2394 | 1.0854 |  |  | 0.2545 | 1.0825 |  |  | 0.2044 | 0.6454 |
| The parameter errors of L2=35km (%) | 0.1504 |  | 0.00003 | 0.0925 |  |  | 0.0082 | 0.0244 |  | 0.0147 |
| The measured value of L3=50km (Ω/km) | 0.2390 |  | 1.0854 | 0.2541 |  |  | 1.0825 | 0.2041 |  | 0.6454 |
| The parameter errors of L3=50km (%) | 0.0041 |  | 0.0004 | 0.0449 |  |  | 0.0112 | 0.1402 |  | 0.0285 |

From the above simulation results, it can be seen that using the different frequency method to measure the zero-sequence impedance parameters of two parallel transmission lines can achieve high accuracy. Whether the self-parameters of the double circuit lines are equal or not, the coupling coefficient between the lines is in the range of 0.4~0.6, and the length of the lines is in the range of 20km~50km, the maximum measurement error of this method is less than 1%, and the minimum error is only four digits after the decimal point, approximately 0, which fully meets the practical measurement requirements of engineering.

3. Measurement and test verification of mutual inductance parameters of double circuit lines with incomplete shutdown mode

3.1 Testing principles

To ensure the accuracy of the mutual inductance parameters of the line, simulation debugging and testing are required. Based on theoretical analysis and simulation model, the simulation scheme of line mutual inductance parameter test under double circuit incomplete shutdown mode in laboratory environment is established, as shown in Figure 5.

FIGURE 5 Schematic diagram of mutual inductance parameter testing for double circuit lines in laboratory environment under incomplete shutdown mode

In the test schematic diagram shown in Figure 5, line 1 is the line to be tested with power failure, and line 2 is the line in normal operation. Simulate the conditions of line 1 by setting the current limiting resistance R and grounding. Z11 simulates the zero-sequence impedance of line 1, and Z22 simulates the zero-sequence impedance of line 2. Z12=Z21 represents the mutual inductance between line 1 and line 2, which is simulated by isolation transformer. To simulate the normal operation of line 2, a voltage transformer is used to replace the power supply S2, and 10V/50Hz AC is applied to the secondary side of the PT. The variable frequency power supply S1 is set at the first end of line 1 with adjustable frequency to verify the output stability of the power supply at different frequencies and voltages. Set current transformer 1 (CT1) at the first end of line 1, current transformer 2 (CT2) at the first end of line 2, and current transformer 3 (CT3) at the end of line 1. Current transformers are used to simulate the current sampling of real lines.

3.2 Data testing and comparative analysis based on test bench

In the physical diagram of the test circuit shown in Figure 6, it is composed of VM06-1100 type variable frequency power supply, isolation transformer, PT voltage transformer, current transformer CT, KEW-8146 type current transformer CT, PT-X-2 high-precision voltage transformer, etc. The isolation transformer is used to simulate the mutual impedance between line 1 and line 2, and the ratio of PT voltage transformer is 10,000:100. The different frequency power supply adopts high-performance vector control inverter, the maximum output power is 120kW, and the output voltage range is 380V ~ 460V. The power supply is connected with the main control unit through the RS-485 interface, and the output voltage and output frequency can be programmed to adjust. The output voltage of the power supply needs to be set at different gears and output to line 1 to verify whether the output of the selected power supply is stable and reliable under different voltage gears. In order to simulate the zero sequence impedances Z11 and Z22 of the circuit, a series connected high-power resistor and inductor were used for circuit construction. The impedance is designed to be Z11=Z22=4.1134+j20.4646 (20.874Ω∠78.635°). The unit value per kilometer of the 110kV voltage class of the analog line is Z11=Z22=0.2056+j1.0232 (1.0437Ω∠78.635°) and the length of the analog line is L=20km.

FIGURE 6 Physical diagram of the test circuit

The test circuit test bench as shown in Figure 6 was used to carry out the test under four working conditions of 50V, 100V, 200V and 500V output voltage of the different frequency power supply. Record the head voltage U10 and terminal voltage U10p of line 1, and the head voltage U20 of line 2. Simultaneously record the frequency difference voltage values at each point when the frequency difference power supply S1 outputs different voltage values, and verify the measurement stability of the voltage sensor at different voltages and frequencies. Record the head current I1 of line 1 (collected by the CT1 secondary current sensor), the first end current I2 of line 2 (collected by the CT2 secondary current sensor), and the end current I1p of line 1 (collected by the CT3 secondary current sensor). By recording current values under different voltages, the measurement stability of current sensors under different frequency currents is verified. All voltage and current data are collected by each sensor at the corresponding measuring point. The data is fed into the measuring device through the signal conditioning circuit and the op amplifier circuit to the device's ADI chip. The zero sequence impedance value Z11 and the mutual inductance value Z12 in the analog line are calculated by using the ARM chip. The test results of the four working conditions are shown in Table 3.

TABLE 3 Test results and comparative analysis of four different frequency power supply output voltages

| title | output voltage 50V |  | output voltage 100V |  | output voltage 200V |  | output voltage 500V |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| frequency | 45Hz | 55Hz | 45Hz | 55Hz | 45Hz | 55Hz | 45Hz | 55Hz |
| U10/ V | 50.04 | 50.17 | 100.26 | 101.13 | 200.76 | 202.14 | 502.74 V | 503.67 V |
| I1/ mA | 26.606 | 22.033 | 53.278 | 44.383 | 106.774 | 88.742 | 267.287 | 221.203 |
| Phase difference between U10 and I1 | -83.347° | -82.804° | -82.452° | -83.013° | -81.984° | -83.115° | -82.487° | -83.198° |
| U20/ mV | 13.619 | 11.003 | 27.257 | 22.140 | 54.651 | 44.314 | 136.43 | 111.06 |
| I2/ mA | 11.350 | 9.170 | 22.730 | 18.465 | 45.494 | 36.876 | 114.196 | 92.065 |
| Phase difference between U20 and I2 | 7.613° | 9.235° | 7.577° | 9.118° | 7.447° | 8.997° | 7.403° | 9.487° |
| Phase difference between U10 and U20 | -90.137° | -92.169° | -90.369° | -92.471° | -90.227° | -92.187° | -90.297° | -92.304° |
| U10p | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| I1p/ mA | 26.606 | 22.033 | 53.288 | 44.393 | 106.694 | 88.712 | 267.297 | 221.203 |
| Z11(Unit value per kilometer) | 0.9469Ω ∠79.324° | 1.1371Ω∠78.479° | 0.9474Ω∠78.429° | 1.1377Ω∠78.688° | 0.9461Ω ∠77.961° | 1.1367Ω ∠78.792° | 0.9476Ω ∠78.464° | 1.1370Ω ∠78.873° |
|  | 0.1754+ j0.9305 | 0.2271+j1.1142 | 0.1900 + j0.9281 | 0.2231 + j1.1156 | 0.1973 + j0.9253 | 0.2209 + j1.1150 | 0.1895 + j0.9284 | 0.2194 + j1.1156 |
| Z12(Unit value per kilometer) | 0.4985Ω∠67.35° | 0.5312Ω∠67.72° | 0.5017Ω∠67.31° | 0.5286Ω∠67.84° | 0.4877Ω ∠67.41° | 0.5319Ω ∠67.88° | 0.4947Ω ∠67.44° | 0.5354Ω ∠67.81° |
|  | 0.1919 + j0.4601 | 0.2014 + j0.4915 | 0.1935 + j0.4628 | 0.1994 + j0.4896 | 0.1873 + j0.4502 | 0.2003 + j0.4927 | 0.1898 + j0.4568 | 0.2022 + j0.4957 |

Through the test results and comparative analysis of the output voltages of 4 different frequency power supplies as shown in Table 3, it can be seen that:

(1)When the output voltage is 50V, Z11=1.0420Ω∠78.90°, compared with the standard self-impedance, the impedance deviation is 0.16% and the angle deviation is 0.26°; Z12 = 0.5148Ω∠67.54°, compared with the standard mutual impedance, the impedance deviation is 0.15%, the angle deviation is -0.09°.

(2)When the output voltage is 100V, Z11 = 1.0425Ω∠78.55°, compared with the standard self-impedance, the impedance deviation is 0.11%, the Angle deviation is -0.08°; Z12 = 0.5151Ω∠67.57°, compared with the standard mutual impedance, impedance deviation 0.21%, angle deviation is -0.06°.

(3)When the output voltage is 200V, Z11 = 1.0414Ω∠78.37°, compared with the standard self-impedance, the impedance deviation is 0.22%, the angle deviation is -0.26°; Z12 = 0.5098Ω∠67.64°, compared with the standard mutual impedance, the impedance deviation is -0.81%, and the angle deviation is 0.01°.

(4)When the output voltage is 500V, Z11 = 1.0423Ω∠78.66°, compared with the standard self-impedance, the impedance deviation is 0.13%, the angle deviation is 0.03°; Z12= 0.5150Ω∠67.62°, compared with the standard mutual impedance, the impedance deviation is 0.19%, the angle deviation is -0.01°.

4 conclusion

(1) Based on the zero-sequence coupling model of transmission line, this paper establishes a simulation model in which the zero-sequence self-parameters of two lines are equal and the zero-sequence self-parameters are unequal. The zero-sequence impedance parameters of two parallel transmission lines are measured and simulated by using the different frequency method. The coupling coefficient of the method is in the range of 0.4~0.6. The measurement error value of line parameters is less than 1% in the line length range of 20km~50km, which proves that the model and method can meet the practical measurement requirements of engineering.

(2) In the case of different frequency power supply levels, the signals collected by the selected voltage and current sensors are calculated. The Z11 zero sequence impedance value and Z12 mutual inductance impedance value are accurate, the impedance error is less than 1%, and the angle error is within ±0.2°, which meets the measurement accuracy requirements of the device. It is proved that the signal acquisition, conditioning, amplification and operation circuits of this test device meet the design requirements of measuring mutual inductance parameters of lines by different frequency method under the environment of double circuit without power failure.

reference

- Liu, Y., Yu, L., Lin, X., Duan, S., Yuan, Z., Liu, T., Xu, M., Shi, X.: Interphase Fault Location Method for Distribution Lines Considering Their Parameter Errors. Southern Power System Technology. 1-10 (2023). https://link.cnki.net/urlid/44.1643.TK.20231019.1726.015

- Marcos R. Araújo, Clever Pereira.: Distance protection algorithm for long parallel transmission lines with no common bus. IEEE Transactions on Power Delivery. 35(2), 1059-1061 (2020).

- Jia, K., Li, L., Yang, Z., et al.: Research on Distribution Network Fault Location Based on Bayesian Compressed Sensing Theory. Proceedings of the CSEE. 39(12), 3475-3485 (2019).

- Dong, J., Li, X., Li, J., et al.: Parameter Modification Method and Influence Analysis of Double-circuit Transmission Lines on the Same Tower. HEBEI ELECTRIC POWER. 42(1), 57-61. (2023).

- Lu D, Liu Y, Liao Q, et al. Time-domain transmission line fault location method with full consideration of distributed parameters and line asymmetry[J]. IEEE Transactions on Power Delivery, 2020, 35(6), 2651-2662.

- Fu J, Song G, Schutter B D. Influence of measurement uncertainty on parameter estimation and fault location for transmission lines[J]. IEEE Transactions on Automation Science and Engineering, 2021, 18(1), 337-345.

- Ruan, K., Liu, J., Gao, F., et al.: A Measurement Method for Zero Sequence Parameter of Long Distance Double Circuit Transmission Lines Based on One Terminal Measurement. Proceedings of the CSU-EPSA. 30(9),103-107 (2018).

- Chen, T., Zhao, X., Wang, J., et al.: Research on Live Measurements Technology for High Altitude Multi-Loop Parallel Transmission Line. YUNNAN ELECTRIC POWER. 42(1), 49-52 (2014).

- Yao, R., Huang, H., Peng, F., Guo, W.: Identification Method of Transmission Line Parameters Based on PMU. Electrical Drive. 38(02),101-103+109 (2019).

- Huang, X., Yang, T., Zheng, X., et al.: Parameter Identification of Short Parallel Double-Circuit Lines Based on PMU Measurements. ELECTRIC POWER. 53(7), 141-148 (2020).

- Gao, M.: Research on Measurement Methods of Zero Sequence Distributed Parameters of Non Full Line Parallel Transmission Lines. Wuhan University, 2022.

- Hu, Z., Fu, C., Ni, S., et al.: Analysis and Simulation of Typical Anti-interference Measuring Methods for Zero Sequence Impedance Parameters of Transmission Lines. Automation of Electric Power Systems. 42(23):174-183 (2018).

Author Introduction:

Xiaojun Zhang (1988.03), male, communication author, senior engineer, master's degree, main research direction: new technologies for transmission line operation and maintenance. zh880420@sina.com

Zeyang Lei (1997.06), male, assistant engineer, bachelor's degree, main research direction: high voltage and external insulation technology of transmission and transformation equipment.

Wenbing Zhuang (1984.04), male, senior engineer, bachelor's degree, main research direction: new technologies for transmission line operation and maintenance, unmanned aerial vehicle inspection.

Foundation item: Supported by the National Natural Science Foundation of China (51479154).