Frequency Safety Demand and Coordinated Control Strategy for Power System with Wind Power and Energy Storage

Xiangyu Zhang, Zijian Shao, Yuan Fu, Yabo Cao

Abstract—According to the constraints of frequency safety indices, rationally utilizing the energy reserve provided by wind power and energy storage to meet the system’s frequency regulation demand is inevitable for the development of a large-scale new energy power system. Firstly, frequency response characteristics and frequency regulation safety indicators required by new energy generation systems were analyzed. Secondly, the frequency dynamic response model of the system with wind power and energy storage was established, and the extreme value time for the virtual inertia response of the system was calculated. Using the extreme time at which the frequency drop is maximum, the virtual inertia time constant of the wind-storage system was evaluated. Additionally, the system inertia and the primary frequency regulation demand were obtained considering the frequency safety indices, and a novel coordinated control strategy for wind power and energy storage to provide the required frequency support was proposed. Finally, a grid-connected wind-storage simulation system was built to verify the superiority of the proposed control strategy. The obtained results indicate that the proposed control scheme flexibly meets the system frequency safety requirements.

Index Terms—Frequency dynamic response, frequency safety requirements, extreme value time, virtual inertia, wind-storage system.

INTRODUCTION

I

n recent years, new energy power generation has been rapidly developing, but the power fluctuations of new energy and the lack of grid connection infrastructure have a significant impact on grid security [1-3]. Particularly, inertia and frequency regulation capability of the power grid with high-penetration of new energy sources cannot be ignored. Insufficient frequency regulation ability of wind turbines integrated to the system is considered as a key reason behind accidents such as UK's "8·9" and South Australia's "9·28" power failure [4-5]. Energy storage can quickly compensate for wind power disturbances and has become an important equipment in regional power grids

This work was supported by National Natural Science Foundation of China (NSFC) under Grants (52277100) and Natural Science Foundation of Hebei Province (E2023502038).

X. Zhang, Z. Shao, Y. Fu and Y. Cao are with the State Key Laboratory of Alternate Electrical Power System with Renewable Energy Sources, North China Electric Power University, Baoding 071003, China (e-mail: zh.xy.sq@163.com).

with a high proportion of new energy [6-8]. Although the grid-connected specifications mandating energy storage standards, there is still a room for improvement on how to use the power from energy storage in conjunction with wind turbines to ensure the safety of the system frequency. This technology is also critical for the development of new energy generation systems.

To improve the efficiency of wind energy extraction, wind turbines are usually operated in maximum power point tracking (MPPT) mode. The wind turbines cannot respond to the change in system frequency and do not have the capability of inertia response or primary frequency regulation while operating under MPPT mode [9-11]. To enhance the frequency stability of power systems with large-scale wind farms, the frequency control technology of wind turbines has been continuously improved. In [12], an overspeed control for de-loaded operation is discussed, where the wind power tracking curve shifts to the right, enabling the unit to reserve a part of its power as active power reserve. However, when a frequency rise event occurs, the wind turbine cannot participate in frequency regulation. In [13], a variable pitch angle control is investigated to limit the captured wind energy at high wind speeds, but timely response cannot be provided due to the slow response speed of the controller. Virtual inertia control of wind turbines is introduced to slow down the frequency fluctuations [14]. A proportional-integral-derivative control scheme is used to implement the current controller for wind turbine’s rotor-side converter to make it respond quickly to the grid’s frequency fluctuations [15-16]. The above control strategy has improved the wind turbine inertia response by adding control to the active power control link, but evaluation of virtual inertia is still a challenge, which complicates the design of controller parameters.

In theory, the energy storage device has an energy reserve, and it can participate in system frequency regulation through controlled injection of active power into the grid. Similar to wind turbines, energy storage can also slow down the rate of change of system frequency through virtual inertia, and it can use the energy reserve to reduce the steady-state deviation of the system's primary frequency by using droop control [17-18]. Considering the dynamic changes in system frequency, [19] improves the transient frequency response by introducing virtual inertia and a droop control proportional coefficient divider in the control system. In [20-21], state of charge (SOC) during the actual operation of energy storage is considered, and an energy-assisted primary frequency regulation strategy is discussed. The strategy is based on the dynamic task coefficient, which aims to achieve both energy storage safety and system frequency stability by combining the SOC with the frequency regulation index. Theoretically, energy storage can accurately track power instructions, and its response speed is much faster than that of traditional synchronous generators. However, the current cost of energy storage is high, and the cost of participating in frequency regulation by relying on energy storage alone is severely limited [22].

With the increasing demand for frequency regulation in new energy power generation systems, relying only on wind turbines or energy storage devices has limited frequency regulation capacity. Therefore, maximizing the benefits of frequency regulation from wind power and energy storage, and achieving coordination between wind power and energy storage, will be the key to improving the frequency stability of the system. In [23], energy storage control considering the SOC and wind turbine pitch control is operated successively to participate in system frequency regulation, but there is no coordination between these devices. The complementary advantages of wind power and energy storage for frequency regulation technology should be further exploited. In [24], a virtual synchronous generator (VSG) control scheme is discussed for coordinating between wind turbines and energy storage devices to provide frequency support. Following the principle that energy storage is given priority to support the gird frequency while the wind turbine completes the remaining frequency regulation tasks, the energy storage capacity configuration in this mode is high. In [25], a virtual inertia controller for the wind turbine and energy storage is introduced to meet the demand of the system inertia, and the speed control module is introduced to restore the initial state after the system frequency is stable. However, the virtual inertia of the wind turbine and energy storage still needs to be evaluated. In [26-27], attention is paid to the power distribution scheme between wind power and energy storage for system frequency regulation, taking into account the problems related to the charge and discharge of energy storage. However, several control parameters required by the evaluation method for providing inertial response through wind turbine and energy storage depend on online monitoring, which is difficult to realize in practical engineering. At present, there is an imperfect evaluation of the virtual inertia of both wind turbine and energy storage, which easily disturbs the start and stop conditions of the frequency controller. Due to the complicated coordination logic between virtual inertia and primary frequency regulation, the development of wind-storage coordinated systems is restricted.

This study aims to solve the shortcomings of the frequency support control of the wind-storage system, further improve the active support of grid-connected wind turbine and energy storage devices, and enhance the system frequency stability. The structure of this paper is as follows: In Section II, the frequency response characteristics and frequency regulation safety requirements of the wind-storage system are analyzed. In Section III, the dynamic frequency response model of the wind-storage system is established, the inertia response time of the system is calculated, and the virtual inertia of the wind-storage is evaluated according to the wind turbine speed response and energy storage power constraints. Section IV analyzes the inertia and primary frequency regulation requirements based on the inertial response time and frequency safety of the wind-storage system. Section V proposes a coordinated control strategy for virtual inertia and primary frequency regulation. Section VI explains the operation of a nine-node power system with high penetration of wind power generation on the controller hardware-in-the-loop platform. Moreover, the dynamic frequency response of the system with the proposed controller is verified. Finally, the key findings of the study are summarized in Section VII.

FREQUENCY SAFETY REQUIREMENTS OF WIND-STORAGE SYSTEM

  - Frequency Response Characteristic of Wind-storage Systems

In the power grid with a high proportion of new energy, only relying on synchronous generators (SGs) cannot guarantee the frequency stability of the system. As shown in Fig.1, taking the frequency drop caused by a sudden increase in load as an example, the dynamic response of system frequency support can be divided into two stages: [t0-tex] and [tex-t2]. In Fig 1, ΔPm and ΔPe are the mechanical power and electromagnetic power of SG, respectively; t0 is the time at which the disturbance is started; t1 is the time at which the primary frequency regulation has started; tex is the moment when the frequency drops to the lowest value; t2 is the time at which the primary frequency regulation has ended.

Inertia response stage (t0-tex): At t0, the system frequency drops rapidly (df/dt<0) due to a sudden increase in the load. In this stage, the wind turbine and energy storage rapidly increase the active power injection into the grid through additional inertia control, and share the frequency regulation task of SG, thus, reducing the rate at which the system frequency drops.

Frequency recovery stage (tex-t2): In this stage, the wind turbine and energy storage with virtual inertia control will absorb power from the power grid, which increases the additional frequency regulation burden on the SG, and even causes secondary frequency drop. Therefore, when the frequency recovers after tex, the inertial response of the wind power and energy storage should be turned off to help the system frequency recover quickly. Although the grid connection standards for wind farms indicate that the inertia response of wind turbine should meet the requirements of Δfdf/dt>0, the differential control may have high-frequency noise during system frequency response process, which can compromise the controller’s performance.

If the time when the frequency drops to the lowest can be predicted under the disturbance of the wind power and energy storage system and adjust the control strategy in time, the additional control effort can be safely removed, effectively avoiding the misoperation caused by the monitoring error of the frequency differential signal. Further, this can help to solve the current problem of virtual inertia evaluation, so as to provide a more reliable calculation method for the inertia demand under the frequency safety of the system, and greatly improve the reliability of the frequency support of the wind power and energy storage coordinated system.

Fig. 1. Dynamic response of wind-storage system

Frequency Safety Requirements of Wind-storage Systems

The frequency safety of the power generation system is mainly determined by three indices, namely, (i) the rate of change of frequency (df/dt), (ii) the maximum frequency deviation (Δfmax), and (iii) the steady-state frequency deviation (Δfst).

(i) Rate of change of frequency: According to the grid connection standards, the protection threshold of the system frequency’s change rate is set to 0.5 Hz/s in the UK and 1 Hz/s in Ireland [28]. Relevant studies in China have shown that the rate at which the frequency of power system with high penetration of wind power should be limited to ±0.5 Hz/s following a power disturbance.

(ii) Maximum frequency deviation: When the load power changes, the maximum frequency deviation constraint dictates that the change in system frequency should not exceed 1 Hz [29]. To prevent the low-frequency load-shedding devices in the power system from operating under large load disturbances, the frequency deviation value is also limited in China. When high-power disturbance events occur, the minimum frequency of the power system cannot be lower than 49 Hz [30].

(iii) Steady-state frequency deviation: The steady-state deviations in the system frequency reflect the new state of the system operation after disturbance, and excessive steady-state deviations will have a serious impact on the safe operation of the system. The steady-state frequency deviations are generally restricted between 49.5 Hz and 50.5 Hz [31]. Further, the frequency regulation time of system frequency is 20s-30s, and the system frequency deviation of 0.033 Hz is taken as the frequency regulation dead zone [32].

At present, online monitoring is the only way to evaluate the frequency support offered by wind-storage system, which makes it difficult to realize early warning and cannot accurately meet the needs of system frequency regulation. Although the wind turbines and the energy storage devices have taken system frequency security into account, the parameter design basis of the virtual inertia and primary frequency regulation is still insufficient. Therefore, reducing the parameter design difficulty and meeting the frequency security requirements are crucial to the wind-storage power generation system.

Virtual inertia evaluation of wind-storage systems

Extreme Time Calculation of Frequency Response

To evaluate the virtual inertia of wind-storage system, the extreme time when the frequency reaches its maximum value is calculated considering the operation of wind turbine and energy storage. To analyze the dynamic characteristics of the system frequency, a frequency response model of the wind-storage system is established.

In Fig. 2, w is the penetration of wind power, Dsys is the damping coefficient, Hg1 is the equivalent inertia time constant of SG considering w, KL is the regulation coefficient of load, R is the adjustment factor of the governor, TG is the inertia time constant of steam turbine, FG is the characteristic coefficient of steam turbine, Δf is the system frequency variation, ΔPd is the perturbation power of the system, ΔPm is the mechanical power of SG, ΔPw, and ΔPB are the power outputs of wind turbine and energy storage devices, respectively. The equivalent inertia, Hg1=Hg(1-w), where Hg is the inherent inertia of SG. ΔPL is the load regulation signal, and ΔPL=KLΔf. The specific values of each parameter are shown in Table 1 [33].

Fig. 2. Frequency response model of wind-storage system

Tab.1 Parameters of frequency response model of wind-storage system

| Parameter | Hg/s | Dsys | KL | R | TG/s | FG |
| --- | --- | --- | --- | --- | --- | --- |
| Range | 4~10 | 0~1 | 0~1 | 0.03~0.05 | 6~10 | 0~1 |
| Value | 8 | 0.5 | 1 | 0.05 | 6 | 0.3 |

According to Fig. 2, the frequency response expression of the aggregate model of the wind-storage system can be obtained as,

(1)

The power output, ΔPm of SG can be expressed as,

(2)

With the additional differential control, the wind turbine and the energy storage have an inertial response similar to that of a SG, which can be superimposed with SG’s inherent inertia, as described in [36]. Thus, the frequency response equation of the system is obtained as,

(3)

where Hs represents the inertial time constant of the wind-storage system and is given as,

(4)

where Hvw and HvB are the virtual inertia of wind turbine and energy storage device, respectively; g is the installed proportion of the SG, and b is the ratio of installed energy storage capacity to the wind turbine capacity.

By substituting power output of the SG, ΔPm, and load regulation signal, ΔPL into (1), the frequency response model of the wind-storage system in the complex domain can be expressed as,

(5)

The second-order differential equation of the system in the time domain can be obtained from (5) as,

(6)

where m is the primary frequency regulation coefficient of SG considering w, and KGLD is the equivalent primary frequency regulation coefficient of the system, which can be expressed as,

(7)

Assuming that there is a load disturbance in the system at t=0 with the initial conditions as,

(8)

Then, the analytical solution for the differential equation of Δf and t can be obtained as,

(9)

where,

(10)

The moment when the derivative of (9) is 0, is the extreme time at which frequency deviations are maximum, and tex can be calculated as,

(11)

As shown in Fig.1, (t0-tex) is the duration for which virtual inertia support from the wind-storage system is provided. Moreover, the changes in the wind turbine's rotor speed and the SOC of the energy storage during this period will be the key parameters to quantitatively evaluate the virtual inertia.

Factors Influencing the Extremum Time

Based on the analysis of the system frequency response model, the extreme value time is closely related to Hs and ΔPd. When the wind power and energy storage do not participate in the system inertia support, according to the parameters listed in Table 1, setting the system to be disturbed at 3 s, and the disturbance amplitude is 0.1 pu. The frequency response of the system with different penetration w of wind power generation, is shown in Fig. 3.

Fig. 3 Frequency response of wind-storage system without additional control

It can be seen from Fig. 3 that as w increases, the parameters df/dt, Δfmax and Δfst of the system also increase, whereas the time tex is almost constant. When w exceeds a certain value, the frequency safety of the system cannot be guaranteed.

When the wind power and energy storage provide the virtual inertia support, setting b is 10%, Hvw and HvB are 8s and 10s, respectively. The frequency response curve of the wind-storage system with different penetration w of wind power generation, is shown in Fig. 4.

Fig. 4 Frequency response of wind-storage system under virtual inertial control

It can be seen from Fig. 4 that the wind turbine and energy storage devices with virtual inertia control can respond to the changes in system frequency. With an increase in w, the inertia of the system increases and the df/dt and Δfmax of the system decrease, whereas the extreme time, tex of the system frequency response increases.

Analyzing the influence of disturbance on the frequency response of the system, according to the typical data in Table 1, when w is set to 30%, the frequency responses of the system under different disturbances are shown in Fig. 5.

Fig. 5 Frequency response of wind-storage system under different ΔPd

It can be seen from Fig. 5 that with an increase of ΔPd, the indices df/dt, Δfmax, and Δfst of the system increase, but the tex of the wind-storage system is almost unchanged. When ΔPd exceeds 20%, the maximum frequency deviation, Δfmax exceeds 1 Hz, and the system cannot meet the frequency safety requirements.

Before the wind-storage system adopts virtual inertia control, an increase in w and ΔPd will increase the values of df/dt, Δfmax, and Δfst of the system. It is not conducive to frequency stability and safety, but the extreme time tex of the system’s frequency response is almost unchanged. Therefore, tex can be estimated in advance based on system parameters and used as an important parameter for evaluating the virtual inertia of wind turbines and energy storage devices.

Virtual Inertia Evaluation for Wind Turbine and Energy Storage Device

Wind turbines have an inherent moment of inertia, Jw, which can suppress its power fluctuations. By introducing a frequency change in the system, the wind turbine can provide virtual inertia to participate in the frequency support of the system. Referring to the definition of the inertia time constant of SG, the virtual inertia time constant, Hvw of the wind turbine can be expressed as,

(12)

where Jvw is the virtual inertia of the wind turbine; r is the angular velocity of the wind turbine’s rotor; e is the angular frequency of the system; Sw is the installed capacity of wind turbine; r0 is the initial angular velocity of the wind turbine’s rotor; Δr is the change in the angular velocity of wind turbine’s rotor; Δe is the change in synchronous speed; and Hw is the inherent inertia time constant of wind turbine.

To ensure the safe operation of the wind turbine, the angular velocity of rotor is generally limited between 0.8 pu and 1.2 pu. It is worth mentioning that Δe is equal to Δf in pu system. According to (12), the virtual inertia provided by the wind turbine considering w and tex can be expressed as,

(13)

Energy storage relies on active power control to utilize energy reserve and provide inertia support to the system. The power from energy storage with virtual inertia control can be expressed as,

(14)

Upon integrating both sides of (14),

(15)

From (15), the virtual inertia of the energy storage is closely related to its output power, so it can be constrained by power limitation in the virtual inertia evaluation. Within the extreme frequency response time, considering the wind power penetration w and the ratio of energy storage to wind turbine capacity b, the virtual inertia provided by energy storage can be expressed as,

(16)

The parameters required in the existing virtual inertia evaluation method are dynamically changing. Without the key parameter tex, design of the control parameters of the wind turbine and energy storage needs to rely on online measurement. Using the time interval (t0-tex), the virtual inertia evaluation method can cut down on the need for a real-time test and facilitate the distribution of inertia in wind-storage system while still meeting the constraint of system frequency safety.

Frequency regulation demand and storage capacity allocation of wind-storage system

Rate of Change of Frequency

Based on the variations and safety requirements of the system frequency, the constraints of df/dt, Δfmax, and Δfst should be taken as the key parameters for the controller design of the wind turbine and the energy storage device.

At the start of the disturbance period, the system’s unbalanced power is the largest and mainly comes from the disturbance power, ΔPd. As a result, the rate of change of frequency, df/dt is the largest. The dynamic response of the system can be expressed as,

(17)

The constraint on the maximum rate of change of system’s frequency is set to 0.5 Hz/s. If df/dt at the initial stage of the load disturbance is less than the preset value, it is guaranteed that the system can meet the constraint on the rate of change of frequency during the whole frequency regulation period. The minimum inertia requirement of the system based on the constraint on the rate of change of frequency is,

(18)

When the rate of change of system frequency does not meet the safety index, additional inertia control of wind power and energy storage is required to keep the rate of change of system frequency within the safety limits. The inertia demand of wind power and energy storage can be expressed as,

(19)

where bH is the ratio of the energy storage capacity for inertial support to wind turbine capacity.

According to (19), the virtual inertia, HWB that the wind turbine and energy storage need to provide to the system is,

(20)

Taking Hg as 6s and (df/dt)|max as 0.5 Hz/s, the virtual inertia demand of wind power and energy storage is calculated from (20), and the corresponding results are shown in Fig. 6.

Fig. 6 Virtual inertia requirements of wind-storage system

According to (20), under the safety constraint of the rate of change of system frequency, the virtual inertia demand, HWB of wind power and energy storage, mainly depends on ΔPd and w. It can be seen from Fig.6 that the system’s inertia support can be met by SG’s inherent inertia when ΔPd and w are low. With the increase of w, the system's ability to deal with power disturbance is weakened. For example, the system can deal with ΔPd less than 7.2% when w reaches 40%. When w reaches 60%, the power disturbance that the system can cope with is less than 4.8%. Thus, it is difficult to deal with typical fault types in the system, where ΔPd can reach 5%, when there is a significant penetration of wind power.

The capacity ratio of the energy storage required for inertia support can be determined as,

(21)

If the required inertia of the wind-storage system is evaluated, the required energy storage capacity for inertia support can be obtained based on df/dt constraint according to (21).

Maximum Frequency Deviation

To prevent the action of the low-frequency load-shedding device during heavy load disturbance, the maximum frequency deviation, Δfmax is set to 1 Hz. When the system meets the minimum inertia requirement, i.e., Hs=Hmin, the parameters α1, β1, C11, and C21 under the constraint of inertia demand can be obtained by substituting Hmin into (10). Further, the extreme time tex of the system's frequency response can be calculated to determine the maximum frequency deviation in the system, which can be expressed as,

(22)

According to (22), when the inertia demand of the system is determined, Δfmax can be regarded as only related to ΔPd and KGLD. Under the constraint of Δfmax, the minimum value of primary frequency regulation coefficient, Kmin1 required by the system can be calculated based on ΔPd, which can be expressed as,

(23)

When the system's primary frequency regulation is insufficient, the energy storage can quickly participate in the system's frequency regulation through droop control. In this case, the power support ΔPb provided by the system can be expressed as,

(24)

where Kb is the fast frequency regulation coefficient of energy storage; and Δfd is the deadband of primary frequency regulation.

The national standard stipulates that the fast frequency regulation coefficient of energy storage should be between 50 MW/Hz and 200 MW/Hz. After the energy storage participates in the system's primary frequency regulation, the primary frequency regulation coefficient Kbmin1 provided to the system can be expressed as,

(25)

where λbF1 is the ratio between the energy storage capacity used for primary frequency regulation and the wind turbine capacity.

According to (25), to meet the requirements of system’s primary frequency regulation, the proportion of energy storage capacity, bF1 required can be expressed as,

(26)

Steady-state Frequency Deviation

With the increase of the proportion of new energy, the system’s primary frequency regulation will decrease and Δfst will increase significantly. According to (9), the steady-state frequency deviation can be expressed as,

(27)

According to the constraints on Δfst and ΔPd, the minimum value of primary frequency modulation coefficient, Kmin2 required for the system is obtained as,

(28)

Considering the analysis of the steady-state frequency deviation constraint presented in Section 1.2, the parameter Δfst is smaller than 0.5 Hz after 30s of disturbance as the constraint condition, which further limits the primary frequency regulation coefficient Kmin3 of the system.

Substituting t1 as 30s in (9), the system’s energy storage frequency regulation coefficient Kmin3 should meet:

(29)

According to (23), (28), and (29), to satisfy the maximum frequency deviation constraint and steady-state frequency deviation constraint simultaneously, the system’s primary frequency regulation coefficient Kmin should be the maximum value among Kmin1, Kmin2, and Kmin3. Further, the primary frequency regulation coefficient Kbmin required for energy storage should be determined based on Kmin as

(30)

The capacity ratio λbF of energy storage used for system’s primary frequency regulation can be expressed as,

(31)

When the primary frequency regulation capacity of the wind-storage system is insufficient, energy storage should be configured according to (31), so that the system constraints of Δfmax and Δfst can be met.

Coordinated control strategy of Wind turbine and energy storage device for frequency support

Allocation Scheme of Virtual Inertia and Primary Frequency Regulation

To improve the efficiency of wind energy utilization and guarantee the economy of wind turbines, the current control of wind farm does not adopt load reduction, so there is not enough reserved capacity to participate in the primary frequency regulation. In this case, the primary way for wind turbines to participate in the frequency support will be through virtual inertia response. Unlike the wind turbines, energy storage devices are flexible. Thus, differential and droop control schemes can be added to energy storage devices to provide power support to the system. In the frequency coordinated control strategy of the wind-storage system, the required inertia is jointly provided by the SG, wind turbine, and energy storage. Moreover, the function of primary frequency regulation is undertaken by the SG and energy storage devices.

For wind turbine and energy storage, both the virtual inertia support and primary frequency regulation need to be determined by the system frequency safety regulations. However, relevant measuring instrument that can directly obtain the online frequency regulation demand for wind power and energy storage is not available.

To clarify the inertia support conditions, the reference disturbance powers ΔPd1 and ΔPd2 required for inertial support, and the reference disturbance power ΔPd3 required for the primary frequency regulation are introduced. By comparing the values of ΔPd and ΔPd1, ΔPd2 and ΔPd3, the inertia and primary frequency regulation requirements can be reasonably allocated.

Combined with (19), (23), and (29), the perturbation reference powers ΔPd1, ΔPd2, and ΔPd3 under the frequency safety constraint can be expressed as,

(32)

The virtual inertia and primary frequency regulation schemes for the wind-storage system are shown in Table 2. According to (32) and Table 2, the frequency regulation instruction for the wind-storage system is generated by figuring out the inertia and the frequency regulation allocation scheme. This is done by judging the interval where the system disturbance is located.

Tab.2 Allocation scheme of wind-storage system

| ΔPd/pu | [0, ΔPd1] | [ΔPd1, ΔPd2] | [ΔPd2, ΔPmax] | [ΔPd3, ΔPmax] |
| --- | --- | --- | --- | --- |
| Hvw_set/s | 0 | Hvw | Hvw | Hvw |
| HvB_set/s | 0 | 0 | HvB | HvB |
| Kb_set | 0 | 0 | 0 | Kb |

In the quantization process, the inertia demand of the system is equal to the inherent inertia of SG, Hg when ΔPd is equal to ΔPd1. The inertia demand of the system is equal to the sum of Hg and Hvw when ΔPd is equal to ΔPd2. If ΔPd is greater than ΔPd2, the inertia demand of the system is equal to the sum of Hg, Hvw, and HvB. If ΔPd is equal to ΔPd3, the primary frequency regulation demand is equal to the equivalent frequency regulation coefficient KGLD. If ΔPd is greater than ΔPd3, the primary frequency regulation demand is the sum of KGLD and Kb.

Coordinated Control Strategy for Frequency Support

To meet the inertia and primary frequency regulation requirements of the wind-storage system, and reduce the power absorbed during the system’s frequency recovery period, a novel coordinated control strategy, as shown in Fig. 7, is proposed for wind turbine and energy storage systems. In the proposed control scheme, there are five modules: (i) frequency regulation demand assessment, (ii) frequency regulation instruction generation, (iii) wind turbine’s virtual inertia control, (iv) energy storage’s virtual inertia control, and (v) energy storage’s primary frequency regulation control.

When the system frequency drops due to insufficient inertia, the wind turbine gives priority to providing virtual inertia. When the wind power output cannot meet the minimum inertia demand of the system, the energy storage device initiates the virtual inertia control. In the frequency recovery stage, the inertial response extreme time, tex is used as the locking condition for wind power and energy storage controllers, to avoid these devices injecting power and making the frequency recovery more burdensome to the system. According to (31), when the system's primary frequency regulation coefficient is insufficient, the primary frequency regulation control of energy storage will start. Similarly, when the system frequency returns to the steady-state frequency deviation range, the primary frequency regulation control of energy storage will stop.

Fig. 7 Coordinated frequency support control structure of wind-storage system

If the wind turbine adopts inertia control, and energy storage adopts inertia control and droop control, the corresponding controller parameters are KwH, KbH, and KbF, which can be expressed as,

(33)

where Hvw_max is the maximum virtual inertia of the wind turbine based on (13).

Switch modules S1 and S2 are added to the proposed virtual inertia control. According to the frequency regulation instructions, when t is less than (t0+tex), the switch module outputs 1 for inertial response, otherwise outputs 0 to block the inertial response. Further, to avoid a sudden withdrawal of the inertia link causing deviations in the system frequency after tex, the controller adds a first-order inertia link.

Simulation studies of Frequency support control strategy of wind-storage system

Simulation Model

To verify the effectiveness of the proposed coordinated frequency support control strategy for wind power and energy storage, a simulation model of the three-generator and nine-node power system, as shown in Fig. 8, is built. The simulation system includes 150×2 MW doubly-fed wind turbines (DFIG), three SGs G1, G2, and G3 with rated capacities of 200 MW, 500 MW, and 200 MW, respectively. The energy storage device with a rated power of 60 MW is installed in the test system, and the load LA is 600 MW.

Fig. 8 Simulation system structure diagram

Accuracy Verification of Frequency Response Model

Taking the test system as an example, the load A is set to increase by 10% at 3s, and tex is estimated as 2.98s by substituting the system parameters into (11), which is taken as the inertia response time of the wind power and energy storage without virtual inertia control. To verify the accuracy of the frequency response model, the parameters shown in Table 3 are considered. The dynamic responses of the system frequency and G2’s active power during a sudden increase in load are shown in Fig. 9.

Tab.3 Simulation parameters

| Parameter | lw/% | ΔPd/pu | Hmin/s | Hvw/s | HvB/s |
| --- | --- | --- | --- | --- | --- |
| Value | 25 | 0.1 | 5 | 0 | 0 |

Fig. 9 Dynamic response of the test system without virtual inertia control

It can be observed from Fig. 9 (b) that the system frequency decreases and G2’s active power increases in response to the change in system frequency when there is a sudden increase in load by 10%. According to the simulated frequency characteristics of the system shown in Fig. 9 (a), the specific analysis results can be obtained by comparing the extreme time tex, the maximum frequency drop Δfmax, the maximum rate of change of frequency (df/dt)max, and the steady-state frequency deviation Δfst, as summarized in Table 4.

Tab.4 Key indicators of system frequency response

| Parameter | tex/s | Δfmax/Hz | (df/dt)max/Hz/s | Δfst/Hz |
| --- | --- | --- | --- | --- |
| Theoretical | 2.98 | 0.531 | 0.44 | 0.342 |
| Simulation | 2.92 | 0.522 | 0.42 | 0.328 |
| error | 2.01% | 1.69% | 4.55% | 4.09% |

Due to the complexities associated with double-loop control, transformer, and lines in the simulation system, theoretical models are simplified, as a result, the calculation results have certain errors. It can be seen from Table 4 that the errors in tex, (df/dt)max, Δfmax, and Δfst indicators are within 5%, verifying the accuracy of the frequency response model.

Frequency Response of Wind-storage System under Coordinated Control

To verify the superiority of the proposed coordinated control strategy (Case3) between wind turbine and energy storage device, the system’s frequency regulation performance during MPPT control (Case1, KwH=0, and KbH=0) and conventional inertia control (Case2, KwH=6, and KbH=10) are compared.

Considering a positive value of ΔPd as an example, the initial speed of the wind turbine, r0 is 0.84 pu. According to (13), the virtual inertia of the wind turbine, Hvw is conservatively evaluated as 6.72s. From (32), the disturbance reference powers, ΔPd1 as 0.12 pu, ΔPd2 as 0.1536 pu, and ΔPd3 as 0.1652 pu are considered, and the following four scenarios are investigated,

In Scenario 1, the wind turbine and energy storage do not participate in frequency support. The disturbance ΔPd is set to 0.1 pu. According to (18), the system’s minimum inertia requirement is 5s, whereas the inertia provided by the SG is 6s. Thus, the wind turbine and energy storage do not need to provide additional inertia.

In Scenario 2, only wind turbine participates in the frequency support. The disturbance ΔPd is set to 0.13 pu, and the system’s minimum inertia demand, Hmin is 6.5s. Since ΔPd1＜ΔPd＜ΔPd2, wind turbine should have the ability to support the system with the required inertia. According to the frequency regulation instructions and simulation parameters, the inertia response time of the wind turbine is 2s, and the energy storage does not need to participate in the system frequency support.

In Scenario 3, wind turbine and energy storage participate in the frequency support. The disturbance, ΔPd is set to 0.16 pu, and the minimum inertia requirement for the system is 8s. Because ΔPd>ΔPd2, the energy storage should have the ability to support the frequency, and cooperate with SG and wind turbine to support the system with the required inertia. According to the frequency regulation instructions and simulation parameters, the inertia time constant of the wind turbine is 6.72s, and that of the energy storage is 12.8s.

In Scenario 4, wind turbine and energy storage participate in the frequency support. The disturbance, ΔPd is set to 0.18 pu. According to (30), the primary frequency regulation requirement of the system, Kmin is 18.01 MW/Hz. Since Kmin>KGLD, the energy storage should have the ability of primary frequency regulation, and cooperate with SG to provide required frequency support to the system.

In Senarios 1-4, the frequency regulation controller parameters for wind turbine and energy storage are shown in Table 5.

Tab.5 Parameter setting in senarios 1-4

| Parameter | ΔPd/pu | Hmin/s | Ksmin | Hvw/s | HvB/s | KwH | KbH | KbF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Scenario 1 | 0.1 | 5 | 10 | 0 | 0 | 0 | 0 | 0 |
| Scenario 2 | 0.13 | 6.5 | 13.01 | 2 | 0 | 4 | 0 | 0 |
| Scenario 3 | 0.16 | 8 | 16.01 | 6.72 | 12.8 | 13.44 | 25.6 | 0 |
| Scenario 4 | 0.18 | 9 | 18.01 | 10.45 | 15.52 | 20.9 | 31.04 | 60.4 |

In Scenario 1, the wind turbine and energy storage device do not need to provide power support to the system, avoiding frequent operation. The frequency response of the system is shown in Fig. 9. As can be seen, the maximum frequency drop Δfmax is -0.522 Hz, the steady-state frequency deviation Δfst is -0.328 Hz, and the maximum rate of change of system frequency df/dt is -0.42 Hz/s, which meets the frequency safety constraints.

Fig. 10 Dynamic response of the test system in senario 2

It can be observed from Fig. 10 (a) that the Δfmax with MPPT control is -0.687 Hz, and Δfst is -0.402 Hz, but df/dt is -0.68 Hz/s at the initial stage of disturbance when ΔPd is 0.13 pu. In this case, the system safety can no longer be guaranteed.

With the conventional inertia control, the wind turbine and energy storage devices provide a fixed inertia support, as a result, df/dt of the system is -0.44 Hz/s and Δfmax is -0.624 Hz at the beginning of the disturbance. Since the conventional inertia control does not exist on time, the wind turbine absorbs power from the system during the frequency recovery period. Consequently, the frequency overshoots, increasing the frequency regulation burden on the system.

With the proposed control scheme, Δfmax and df/dt of the system are -0.631 Hz and -0.47 Hz/s, respectively. Although the frequency regulation indicators are not much different from the effect of conventional inertia control, the inertia control can exist on time at tex, and the overshoot decreases significantly in the process of system frequency recovery.

In addition, after the inertia control exits, an inertial link is added to the control system so that the wind power does not drop instantaneously, but rather exits smoothly. In Scenario 2, the wind power provides fixed inertial support of 3s with the conventional inertia control, while it only needs to provide 2s of inertial support to meet the system requirements in the proposed scheme. In the conventional case, the wind turbine provides surplus power to the system. It can be seen from Fig. 10 (b) that the wind turbine output decreases with the proposed control, reducing the wind power fluctuations, which is more conducive to the stable operation of the wind turbine. Since the disturbance does not trigger the conditions of inertia control or primary frequency regulation control, the energy storage does not need to respond to the system frequency deviations.

Fig. 11 Dynamic response of the test system in senario 3

It can be seen from Fig. 11 that Δfmax and Δfst of the system with MPPT control are -0.817 Hz and -0.492 Hz, respectively, when ΔPd is 0.16 pu. The df/dt at the initial stage of disturbance is -0.81 Hz/s, and it does not meet the system’s frequency safety index. When the conventional inertia control is adopted, Δfmax of the system is -0.756 Hz and df/dt is -0.65 Hz/s, which do not meet the frequency safety constraints. Furthermore, the wind turbines and energy storage devices absorb power during the system’s frequency recovery period, which is not conducive to the stable operation of the system.

By adopting the proposed control, Δfmax and df/dt of the system are reduced to -0.684 Hz and -0.42 Hz/s, respectively, which meet the frequency safety requirements of the system. The inertia control can exist on time at tex, and the overshoot is minimized during the system frequency recovery. Moreover, the power injected by wind turbine and energy storage devices can ramp down smoothly. It can be seen from Fig. 11(b) that Δfst in Scenario 3 is less than 0.5 Hz, and the energy storage does not need to start the primary frequency regulation. However, since the disturbance, ΔPd of 0.16 is closer to ΔPd3 of 0.1652, the steady-state frequency deviation is closer to the constraint limit.

Fig. 12 Dynamic response of the test system in scenario 4

As the disturbance ΔPd set in Scenario 4 is greater than ΔPd3, the energy storage should activate the primary frequency regulation to participate in the system frequency support. It can be seen from Fig. 12 that Δfmax with MPPT control is -0.955 Hz when ΔPd is 0.18 pu, which is closer to the constraint boundary of maximum frequency variation. The df/dt and Δfst of the system are -0.95 Hz/s and -0.566 Hz, respectively, which do not meet the frequency safety constraints. Under the conventional inertia control, df/dt of the system is -0.69 Hz/s, which does not meet the frequency safety index.

By adopting the proposed control, Δfmax and df/dt of the system are -0.674 Hz and -0.47 Hz/s, respectively. The primary frequency regulation control of energy storage increases the active power to compensate for the shortfall in the SG's primary frequency regulation capability. As a result, Δfst is reduced from -0.566 Hz to -0.491 Hz, meeting the requirement of system frequency safety.

The system’s frequency response in Scenario 1-4 shows that tex was almost unchanged (approximately 5.9s) with MPPT control. With the conventional inertia control, tex is almost constant at approximately 6.6s. In the proposed coordinated control, tex increases, which is consistent with the extreme time change rule of the wind-storage system discussed in Section 2.2. This verifies the applicability of the proposed frequency response model.

In summary, the proposed control strategy fully explores the potential of wind turbines and energy storage devices. The inertia support stops within the extreme frequency response time, reducing the overshoot during system frequency recovery. It is conducive to system frequency recovery, and the frequency regulation effect has significant advantages over conventional frequency support control. In addition, according to the system inertia and primary frequency regulation demand, the disturbance is divided into intervals to determine the participation of wind turbine and energy storage in the system frequency regulation, which makes it simple and reduces the implementation difficulties.

Conclusions

To improve the frequency stability of the power grid with high penetration of wind power generation, a novel coordinated control strategy between wind turbine and energy storage device based on the system's frequency regulation requirements is proposed. Through theoretical analysis and simulation verification, the following conclusions are obtained:

1) The wind turbine and energy storage devices can adopt virtual inertia and primary frequency regulation control to participate in system frequency regulation. The control should reasonably utilize the system’s energy reserve while taking into the three safety requirements, namely, rate of change of system frequency (df/dt), the maximum frequency deviation (Δfmax), and the steady-state frequency deviation (Δfst).

2) By establishing the frequency response model of the wind-storage system, the frequency response extreme time is calculated to estimate the virtual inertia of the system. Furthermore, the extreme time can be used as a locking condition for the virtual inertia support. The test results show that the proposed control can effectively avoid the frequency overshoot during the frequency recovery period and meet the frequency safety indices.

3) With the proposed coordinated control strategy, the virtual inertia and the primary frequency regulation instructions of the wind-storage system are generated to meet the key indicators of the system’s frequency stability requirements during a specified disturbance power interval. The test results demonstrate that the frequency regulation task can be effectively allocated between the wind turbine and energy storage device, meeting the system’s frequency support requirements more reliably.

references

[1] Q. Wu, Y. Huang, C. Li, Y. Gu, H. Zhao and Y. Zhan, "Small Signal Stability of Synchronous Motor-Generator Pair for Power System With High Penetration of Renewable Energy," in IEEE Access, vol. 7, pp. 166964-166974, 2019.

[2] B. Spichartz, K. Günther and C. Sourkounis, "New Stability Concept for Primary Controlled Variable Speed Wind Turbines Considering Wind Fluctuations and Power Smoothing," in IEEE Transactions on Industry Applications, vol. 58, no. 2, pp. 2378-2388, March-April 2022.

[3] X Zhang, H Liu, Y Fu, Y Cao, and Y Li. "Virtual shaft control of hybrid energy storage for oscillation suppression by transient energy capture." International Journal of Electrical Power & Energy Systems vol 157, pp 109794, 2024.

[4] N. G. ESO, “Technical report on the events of 9 August 2019,” Tech.Rep. Sep. 2019. Accessed: Jul.2022. [Online]. Available: https://www.nationalgrideso.com/document/152346/download.

[5] AEM Operator, “Preliminary report: Black system event in South Australia on 28 September 2016,” Tech. Rep. Oct. 2016. Accessed: Jul. 2022. [Online]. Available: https://apo.org.au/node/68095.

[6] M. -S. Lu, C. -L. Chang, W. -J. Lee and L. Wang, "Combining the Wind Power Generation System With Energy Storage Equipment," in IEEE Transactions on Industry Applications, vol. 45, no. 6, pp. 2109-2115, Nov.-dec. 2009.

[7] Y. Cheng, R. Azizipanah-Abarghooee, S. Azizi, L. Ding, and V. Terzija, ‘‘Smart frequency control in low inertia energy systems based on frequency response techniques: A review,’’ Appl. Energy, vol. 279, Dec. 2020.

[8] X. Hou, Y. Sun, X. Zhang, J. Lu, P. Wang, and J. M. Guerrero, ‘‘Improvement of frequency regulation in VSG-based AC microgrid via adaptive virtual inertia,’’ IEEE Trans. Power Electron., vol. 35, no. 2, pp. 1589–1602, Feb. 2020.

[9] D. Gautam, L. Goel, R. Ayyanar, V. Vittal and T. Harbour, "Control Strategy to Mitigate the Impact of Reduced Inertia Due to Doubly Fed Induction Generators on Large Power Systems," in IEEE Transactions on Power Systems, vol. 26, no. 1, pp. 214-224, Feb. 2011.

[10] Y. Zhao et al., "Integrated Assessment of the Reliability and Frequency Deviation Risks in Power Systems Considering the Frequency Regulation of DFIG-Based Wind Turbines," in IEEE Transactions on Sustainable Energy, vol. 14, no. 4, pp. 2308-2326, Oct. 2023.

[11] V. Gevorgian, Y. Zhang and E. Ela, "Investigating the Impacts of Wind Generation Participation in Interconnection Frequency Response," in IEEE Transactions on Sustainable Energy, vol. 6, no. 3, pp. 1004-1012, July 2015.

[12] Z.-S. Zhang, Y.-Z. Sun, J. Lin, and G.-J. Li, “Coordinated frequency regulation by doubly fed induction generator-based wind power plants,” Inst. Eng. Technol. Renewable Power Gener., vol. 6, pp. 38–47, Jan. 2012.

[13] R. Cardenas, R. Pena, S. Alepuz and G. Asher, "Overview of Control Systems for the Operation of DFIGs in Wind Energy Applications," in IEEE Transactions on Industrial Electronics, vol. 60, no. 7, pp. 2776-2798, July 2013.

[14] D. Ochoa and S. Martinez, “Fast-frequency response provided by DFIG-wind turbines and its impact on the grid,” IEEE Trans. Power Syst., vol. 32, no. 5, pp. 4002–4011, Sep. 2017.

[15] H. Habibi, H. Rahimi Nohooji and I. Howard, "Adaptive PID Control of Wind Turbines for Power Regulation With Unknown Control Direction and Actuator Faults," in IEEE Access, vol. 6, pp. 37464-37479, 2018.

[16] W. C. Wong and C. Y. Chung, "Coordinated Damping Control Design for DFIG-Based Wind Generation Considering Power Output Variation," in IEEE Transactions on Power Systems, vol. 27, no. 4, pp. 1916-1925, Nov. 2012.

[17] J. Fang, Y. Tang, H. Li and X. Li, "A Battery/Ultracapacitor Hybrid Energy Storage System for Implementing the Power Management of Virtual Synchronous Generators," in IEEE Transactions on Power Electronics, vol. 33, no. 4, pp. 2820-2824, April 2018.

[18] X. Zhang, Z. Zhu, Y. Fu and W. Shen, “Multi-objective virtual inertia control of renewable power generator for transient stability improvement in interconnected power system,” in International Journal of Electrical Power & Energy Systems, vol. 117, pp. 105641, May 2020.

[19] Zhang, Bo, et al. "Economic analysis and configuration design for the energy storage unit of photovoltaic virtual synchronous generator based on the inertia support and primary frequency control." in International Journal of Electrical Power & Energy Systems, vol 134, pp 107349, 2022.

[20] C. Sun, G. Joos and F. Bouffard, "Adaptive Coordination for Power and SoC Limiting Control of Energy Storage in an Islanded AC Microgrid With Impact Load," in IEEE Transactions on Power Delivery, vol. 35, no. 2, pp. 580-591, April 2020.

[21] X. Lu, K. Sun, J. M. Guerrero, J. C. Vasquez, and L. Huang, “Stateof-charge balance using adaptive droop control for distributed energy storage systems in DC microgrid applications,” IEEE Trans. Ind. Electron., vol. 61, no. 6, pp. 2804–2815, Jun. 2014.

[22] Wang, Sen, et al. "Analysis of energy storage demand for peak shaving and frequency regulation of power systems with high penetration of renewable energy," in Energy vol 267, pp 126586, 2023.

[23] J. Dang, J. Seuss, L. Suneja and R. G. Harley, "SoC Feedback Control for Wind and ESS Hybrid Power System Frequency Regulation," in IEEE Journal of Emerging and Selected Topics in Power Electronics, vol. 2, no. 1, pp. 79-86, March 2014.

[24] X. Hou, Y. Sun, X. Zhang, J. Lu, P. Wang, and J. M. Guerrero, ‘‘Improvement of frequency regulation in VSG-based AC microgrid via adaptive virtual inertia,’’ IEEE Trans. Power Electron., vol. 35, no. 2, pp. 1589–1602, Feb. 2020.

[25] S. Zhang, Y. Mishra, and M. Shahidehpour, “Fuzzy-logic based frequency controller for wind farms augmented with energy storage systems,” IEEE Trans. Power Syst., vol. 31, no. 2, pp. 1595–1603, Mar. 2016.

[26] L. Miao, J. Wen, H. Xie, C. Yue and W. -J. Lee, "Coordinated Control Strategy of Wind Turbine Generator and Energy Storage Equipment for Frequency Support," in IEEE Transactions on Industry Applications, vol. 51, no. 4, pp. 2732-2742, July-Aug. 2015.

[27] X. Wang, J. Zhou, B. Qin and L. Guo, "Coordinated Power Smoothing Control Strategy of Multi-Wind Turbines and Energy Storage Systems in Wind Farm Based on MADRL," in IEEE Transactions on Sustainable Energy, vol. 15, no. 1, pp. 368-380, Jan. 2024.

[28] Azizipanah-Abarghooee, Rasoul, et al. "Integration of wind and solar energies with battery energy storage systems into 36-zone Great Britain power system for frequency regulation studies," in International Journal of Electrical Power & Energy Systems vol 156, pp 109737, 2024.

[29] X. Meng, J. Liu and Z. Liu, "A Generalized Droop Control for Grid-Supporting Inverter Based on Comparison Between Traditional Droop Control and Virtual Synchronous Generator Control," in IEEE Transactions on Power Electronics, vol. 34, no. 6, pp. 5416-5438, June 2019.

[30] Operator, Australian Energy Market. "Inertia requirements methodology inertia requirements & shortfalls." Australian Energy Market Operator (AEMO): Melbourne, Australia (2018): 46.

[31] Ju, **, et al. "Analytic assessment of the power system frequency security," in IET Generation, Transmission & Distribution, vol. 18, pp. 2215-2225, August 2021.

[32] Attya A B, Dominguez-Garcia J L, Anaya-Lara O, "A review on frequency support provision by wind power plants: Current and future challenges," in Renewable and Sustainable Energy Reviews, 81, no. 2, pp. 2071-2087, January 2018.

[33] Q. Shi, F. Li and H. Cui, "Analytical Method to Aggregate Multi-Machine SFR Model With Applications in Power System Dynamic Studies," in IEEE Transactions on Power Systems, vol. 33, no. 6, pp. 65-6367, Nov. 2018.