Field analysis of directionality measurement with Inverter based resources in India

Ashoka Shyamaprasad1 5*, K. P. Vittal2, Praveen A N3, O. D. Naidu4

1Hitachi Energy Sweden AB, Grid Integration, Västerås, Sweden

2Department of Electrical Engineering, NITK, Surathkal, Karnataka, India

3Hitachi Energy LLC, Grid Automation, Dubai, UAE

4Hitachi Energy Research, Bangalore, India

5Hitachi Energy India.Ltd, Grid Automation, Peenya, Bangalore, India

* ashoka.shyamaprasad@ hitachienergy.com

Abstract:   Power system protection has evolved over decades. A step change occurred when communication aspects were introduced as part of IEC 61850 during the late nineties. Renewable energy penetration into power network especially into high voltage levels has been yet another big step. Protection engineers are facing challenges with traditional relay algorithms and the way relays are set in the substation. The primary reason could be attributed to the characteristics of renewable source which differ from the characteristics of traditional grid in many ways. Studies and field analysis are on-going, and engineers are continuously striving to optimize relay design, practices, as well as settings considering the aspects related to inverter design. The detection of directionality in distance relay and response for various type of system faults is a key area to be considered. The objective of this paper is to analyse the performance of directional elements in a distance protection for a DER (Distributed Energy Resource) connected system in India. In addition, the aim is to understand the gaps from existing research to the behaviours of the current directional protections which would help in identifying mechanisms to ascertain directionality for similar systems in the future.

Introduction

Over the past few decades, the conventional grid has been changing in terms of generation, transmission, distribution of power. The technologies are evolving day by day and are supporting to overcome the challenges faced by utilities, consumers as well as system operators. The government policies are also supporting the fast implementation in much structured and controlled way. With more and more focus on managing carbon footprint, technologies have been helping power sector to have distributed energy resources to be installed and integrated to existing network.

Renewable generation is expected to reach 80–90% of the global energy mix by 2050 as the global build-out rates for solar and wind grow by a factor of 5 and 8 respectively [1]. Further, renewable energy source share is expected to double in the next 15 years, from 29% to 60%. Installation of solar and wind-based power plants are available at a lower cost than existing fossil fuels in most countries and are projected to become increasingly cost competitive globally. These generation are termed as power electronics or Inverter Based Resources (IBR), since they are connected to the power network fully or partially through power electronic converters. Inverters can adjust the voltage and current waveforms they deliver as an electrical source. Hence inverters could respond more quickly and flexibly than directly coupled sources. Response of these inverters is more software-defined and provides high level of flexibility and unique performance characteristics and opportunities. Based on their design and control strategies, IBR have different fault characteristics from traditional synchronous generators (SG) [2]. Hence, increased penetration of IBRs in the power system has started to impact the performance of traditional protective relay schemes which have been set under the assumption of a SG-dominated power system. It has started posing challenges to Protection engineers and need for developing remedial solutions ensuring the effectiveness of system protection under higher levels of IBRs [3].

This paper presents three case studies from Indian grid- two from wind plants (Type-3 and Type-4 wind plant) and one from solar plant. The disturbance reports from relays at both Grid end and DER end have been analyzed. A generic solution for directionality in distance protection addressing the challenges from each type of IBR is proposed and validated with the same disturbance.

This paper is organized as follows. Section II details the literature study conducted on impact of renewable penetration to directional element.  Section III presents the basic operation and performance of directional relay and the theory behind the way algorithms are developed in commercially available relays. Section IV presents the analysis summary from the field data analysis by re-running the disturbance report and identifying the areas where the algorithms have worked as expected and the areas where we see differences. Section V presents discussions based on the analysis. Section VI concludes the paper and identifies the next steps.

Literature Study

There have been attempts to capture and study the behaviour of protection relays across the globe after IBRs started penetrating the power network. Reports published in North America [4] claim that protection system mis operations are quite significant and are main contributors to automatic transmission outage severity. The impact are also more than any other transmission events and if these are taken care of suitably, it would help in improvement of system reliability. The mis operations are periodic, with peaks in the spring and summer months. The top 3 reasons contributing to over 60% of all mis-operations are.

- Incorrect setting/logic/design errors

- relay failures/malfunctions

- communication failures

One other important player WECC also has reported mal operations in their research report during 2017 [5]. The above data was once again reconfirmed during Dec 2021by US Department of Energy [6] and also highlighted  type of primary cause, equipment type affected and on relay technology adopted.  The complexity of new relay technology also contributes to mis operations. The relay flexibility in terms of programming multiple functions has become the industry norm.

The main drivers for growth of renewable energy sources are the declining cost and improved technology [7].  Proportion of non-fossil generation capacity expected to rise from 33% in 2018 to 40% by 2030 (GoI, 2015). India’s RE potential is much higher, with wind being 300 GW (National Institute of Wind Energy, 2015), and solar being 748 GW (MNRE, 2014). This implies that there is enough scope to scale up RE generation at the national level with declining cost.

The Renewable Energy Management Center (REMC) in Southern Region Load Dispatch Center (SRLDC) in India, captured experience on various aspects of renewable energy and its associated challenges way forward to handle the future additions [8]. Around 30 major tripping cases in southern region during 2013 to 2021 affecting RE generation were discussed. Loss of wind generation due to improper setting of anti-islanding relay was reported. The global energy scenario with Indian context and the challenges faced in renewable energy generation and policies of Indian government to establish this generation throughout India has been evaluated and reported [9].

The directional element together with distance relay, [10], [11] has been a practice in the power system protection and is believed to  increase the security of system [12]. It is important to choose correct polarizing and operate signals for the correct phase or phase pairs or symmetrical component quantities. The impact on implementation, cost, security, and sensitivity are also key parameters to consider.

The protection engineers started facing challenges while using directional relays in systems with Type-3 and Type-4 wind energy sources [13],[14]. The fault current magnitudes hardly increase above the full-load current unlike in synchronous generators. The distortion in fault signals together with change in the angle difference between the fault voltage and fault current has been affecting the identification of correct fault direction. Research is needed to find solutions for system reliability issues by relay manufacturers along with energy source manufacturers so that better directional protection algorithms can be developed where Type-3 and Type-4 wind-based generators are deployed [15].

Adaptive and non-adaptive relaying could help to overcome impact of renewable integration in different power system networks like distribution, transmission and micro grid systems [16]. Dynamic dependency on the fault levels and need of adaptive schemes, use of logic-based protections could be beneficial in the future compared to conventional schemes [17].

The negative sequence component-based computation philosophies became popular over the years [18] and handled challenges faced in different system configurations. The distance relay near IBR might not operate correctly whereas, the relay near external system ac grid will operate correctly and the zero-sequence current protection operates correctly without any impact [19]. Reliable ground protection, largely independent of the converter source behaviour, can be designed using zero sequence relaying if the interconnecting transformer to the line is a source of zero sequence current in case of Type-3 wind turbines together with STATCOM [20] showing that the negative sequence relaying is not reliable to protect the lines connecting power electronic sources.

The characteristics of IBR compared to SGs are different and would impact various protection schemes on the fault response [3], [21]. Even the sequence components show different behaviour. The positive sequence current is controlled and limited in magnitude. Negative sequence quantities are absent in most of the cases except in few cases, where Grid Codes mandate negative sequence current injection. The negative sequence current increases with the increased gain of IBR and in that case positive sequence current decreases since the total amplitude of the converter current is limited. Inverter also suppresses zero sequence currents to maintain balanced current. However, owing to transformer configuration, zero sequence current might be available at point of common coupling in cases where faults involve ground path. The positive-sequence current (I1) and negative sequence current (I2) contributed by a Type-4 IBR will result in a current amplitude close to nominal load current.

The impact due to negative sequence-based method on directional detection in line faults might result in maloperation [22]. Emulation of the behaviour of electromechanical relays could help in changing the angular characteristics between negative sequence voltage and current and change the fault response of inverters.

The fault current of an IBR has a dynamically changing phase angle depending on IBR control scheme and the amplitude of inverter terminal voltage. Further, in contrast to a SG whose fault current is a factor of physical network, inductive or resistive depending on nature of fault, the fault current of an IBR is influenced by inverter controls and may result in resistive, capacitive, or inductive fault current [24] .

In case of overcurrent protection, the current magnitude, during fault is different value when fault is detected and after fault detection is done [25]. This means IBR fault currents show an initial inception current with a duration from a quarter to two cycles with a magnitude that can be as high as 2.5 p.u followed by a relatively low magnitude fault current with  a short duration (100 ms), limited by the inverter controls to protect the IBR power electronics.

The protection elements which work based on negative sequence quantities also have performance impact due to wind generation [26], [27], [28].  The potential protection mis-operation issues and possible solutions considering different types of wind energy resources with German grid codes were discussed and use of gain characteristics as design parameter, adjusting the relay settings in a smart way were also highlighted to reduce mal operations. They don’t consider behaviour with solar energy resources which was more elaborated in article [29].

The experience of Sandia Lab with IBR together with few utilities in the US based on practical installation was discussed in [30]. Some of the maloperation scenarios linked with the negative-sequence directional element and phase selection were attributed to the currents injected by the IBR. The directional element could be considered as dependable for double line to ground faults as well as two phase faults, but not for 3 phase faults. The results from the simulation showed that phase directional element may misbehave when a three-phase fault disconnects the IBR from the power system.

A new method to enhance the integration of utility-scale IBRs by eliminating any costs related to protective equipment upgrades is preferred way to go [31]. Managing inverter control scheme by altering the currents once the fault type is identified to produce unbalanced currents which emulate synchronous generator fault behaviour is evaluated. The negative-sequence directional relay function and the phase selection is not adaptive because of the complex features of the converter in case of protection for offshore wind farm [32].

The lessons learnt after detailed analysis of real cases from the field were published during 2021 by rerunning the fault waveforms in the relay especially on behaviour of the directional relays [21]:

- The relationship of negative sequence current phase angle with negative sequence voltage for a Type-3 wind plant cannot be estimated unlike that of conventional synchronous sources. Therefore, a conventional relay based on negative sequence current will not be able to provide reliable directional detection against ground faults during high penetrations of IBR. However, if plants are connected through a transformer which could act like a source of zero sequence current, then earth fault detection can be achieved by measuring zero sequence current.

- The protection could also be independent of type of wind turbine generator, or the control algorithm used due to the use of interconnecting transformer.

- In case of Type-4 wind turbine plant the behaviour is different compared to Type-3 wind plant. When the plant has limited capability to inject negative sequence current it would negatively impact the performance of negative-sequence directional relay because the fault current is not able to meet the minimum threshold limit of operation.  This means that relay behaviour is unpredictable.

- When it comes to solar plant, the control algorithm restricts the magnitude of negative sequence current during unbalanced faults and hence, the negative sequence based directional relaying cannot be reliably applied on a line connecting a solar facility.

To overcome the issues faced using superimposed quantities theory, to derive phase selection and directionality in most of the relays in the market, a new adaptive window method is proposed [33]. A dual current controller (DCC) method could ensure enhanced grid reliability by enabling right phase selection [34] that regulates the inverter’s negative-sequence and positive-sequence currents to simultaneously meet phase selection and grid code requirements.

The directional element and its challenges faced due to introduction of IBRs and solutions proposed by researchers across the globe has been a key research area [35]. The various polarizing and operating quantities, phase selection logic complemented by negative sequence and zero sequence elements become important in detecting earth faults in transmission lines. The response during lack of negative sequence current and the impact on distance measurement is equally significant. Even after so many years after introduction of IBRs, the review concludes that further in-depth study of protection schemes is still required, as phasor domain-based functions pose more and more challenges and the solutions with modification of the traditional schemes could reach a point where the solutions become very complex to implement or expensive to acquire or even reduce the sensitivity of equipment.

Previous authors have addressed impedance reach and phase selection in distance protection. Directionality in distance protection and its challenges in IBR interface system is not addressed adequately [13], [14], [15], [20], [30], and [36]. In this context, focus has been made to study various Indian grid mal operations especially where IBRs are integrated into main grid. The field data has been analysed to understand behaviour of the existing protective relays and its algorithms. The findings will help us to further optimize the settings and algorithms in a way that maloperation could further be reduced and could help in improving system reliability and stability.

Directionality Detection Methods

Distance protection has mainly 3 elements – impedance reach, phase selection and directionality. The current distance protection relays have independent measurement of impedance for each fault loop for each phase. It would work together with a sensitive and reliable in-built phase selection scheme making the relay suitable for specific applications like auto-reclosing. The directional relays have been used to ascertain the direction of faults which helps in optimally isolate the faulty section. They complement the primary protection and are designed such that a phase change between a polarized quantity (mostly voltage) and an operational quantity (mostly current) determine the direction of fault. There are features which make protection zones operate independently of each other in directional (forward or reverse) or non-directional mode. This makes them suitable, together with different communication schemes, for various applications of the system with lines and cables in complex network configurations, such as parallel lines, multi-terminal lines [37], [38].

Without loss of generality, a three-bus equivalent system with conventional sources on one end and DER on other end as shown in Fig.1 is considered for the study of directional challenges.

Fig.1. System with one end conventional and other end IBR

Two distance relays 𝑅1 and 𝑅2 are placed on bus M and bus N respectively. Zones 1, 2, and 3 are set in forward direction and Zone 4 is set in reverse direction for the line section MN [21]. The directionality is determined based upon criteria as discussed in the further sections.

Fig.3. Negative Sequence Diagram

Positive sequence based method:

Fig.2. Positive Sequence Diagram

The positive sequence diagram of the system could be written as in Fig.2.

The positive sequence voltage 𝑉1𝑀 can be expressed as

| V1M = I1MN ZMF1 | (1) |
| --- | --- |
| Hence, I1MNV1M= 1ZMF1 | (2) |

The positive sequence angle ∅1 in terms of V1M  and I1MN can be expressed as

∅1  = ∠I1MN-∠ V1M

Hence,

∅1 =-∠ZMF1 					(3)

where, ZMF1 is the positive sequence impedance of line section MN till fault point. Now the direction of the fault can be determined with criteria in Table 1.

Table 1 Positive Sequence directionality criteria [38]

| Angle | Condition | Direction |
| --- | --- | --- |
| ∅1 | -15 deg<∅1<115 deg | Forward |
| ∅1 | Otherwise | Reverse |

The angle is considered based on general application consideration of transmission lines considering compensated and non-compensated lines as well as eliminating effects of load encroachment problems in some cases as discussed in [38].

  - Negative sequence based method:

In case of detection using negative sequence method for the same figure we can draw the sequence network as in Fig.3.

The negative sequence voltage V2M can be expressed, [21].

V2M=-I2MN(ZSL2+ZLM2) 			(4)

Hence,

I2MN-V2M= 1ZSL2+ZLM2 				(5)

The negative sequence angle ∅2 in terms of V2M  and I2MN can be expressed as

∅2= ∠I2MN - ∠-V2MN

Hence,

∅2=-∠(ZSL2+ZLM2)  				(6)

where, ZSL2 is the negative sequence impedance of source 1 and ZLM2 is the negative sequence impedance of line section MN.

The directionality can be determined as per criteria in Table 2 below. The same consideration as discussed in positive sequence detection method on the angle is applied even in this case.

Table 2 Negative Sequence directionality criteria [38]

| Angle | Condition | Direction |
| --- | --- | --- |
| ∅2 | -15 deg<∅2<115 deg | Forward |
| ∅2 | otherwise | Reverse |

  - Zero sequence based method:

Fig.4. Zero Sequence Diagram

For the same system with zero sequence network could be applied and could be shown as in Fig.4.

The zero-sequence voltage V0M can be expressed as [21], [30]

V0M= -I0MN(ZSL0+ZLM0) 			(7)

I0MN-V0M= 1ZSL0+ZLM0 				(8)

The zero-sequence angle ∅0 in terms of V0M  and I0MN can be expressed as

∅0= ∠I0MN - ∠-V0MN=-∠(ZSL0+ZLM0)        (9)

where, ZSL0 is the zero-sequence impedance of source 1 and ZLM0 is the zero-sequence impedance of line section MN.

The directionality criteria could be expressed as in Table 3.

Table 3 Zero Sequence directionality criteria [38]

| Angle | Condition | Direction |
| --- | --- | --- |
| ∅0 | -15 deg<∅0<115 deg | Forward |
| ∅0 | otherwise | Reverse |

The angle considered again is based on general application consideration of transmission lines as already discussed earlier. The same principle could be applied, and the fault direction could be determined for various types of faults.

- at F1 – in zone fault in the protected section MN – fault in forward direction for R1 and R2

- at F2 at bus M fault in forward direction for relay R2 and reverse for R1

Fault at node N is fed only from conventional source, behaviour of both R1 and R2 will hence not have any significant changes. Thus, same scenario is not discussed further in the paper.

  - Fault Detection summary:

When we have conventional sources at both ends for different types of faults, we can infer that with any computation method mentioned above, the directionality is ascertained. However, with one end IBR, the positive sequence computation method works well for most of the cases essentially because the IBR fault current magnitude is 100-120% of the rated load current [3], [39]. The requirement on speed of detection, however, is not addressed by the authors.

When negative sequence method is adapted, it works only in few cases. This is mainly because in most of the inverters even for unbalanced faults in the power system, there is hardly any negative sequence contribution unless mandated by specific grid codes. Hence, the total fault current is limited by the rating of the electronic circuitry and inverter control systems also partially or fully suppress negative sequence current output. This is attributed to missing inertia compared to SGs and shift of angle due to fast response of the inverter compared to SGs. In turn the negative sequence directionality is affected and in most of the cases it is not ascertained. The similar observation is made in case of zero sequence method, and it goes to the extent that even at grid end the directionality is not ascertained for some of the cases. The detailed comparison of the behaviours in both cases have been tabulated in Table 4. For negative sequence-based computation cases where protection fails to ascertain directionality, the cell is highlighted as “N.D” referring to “Not detected” due to the behaviour of inverters which is impacting the impedance angle or angle between I2 and V2.

In case of zero sequence-based method which are effective in case of asymmetrical ground faults, the angle oscillates between the operate and non-operate zones and finally could settle in any area and is termed in the table as “On margin”. The field cases in the reference articles establish these behaviours.

Summary of field cases from India:

For evaluating and analysing the facts mentioned in the literature review, it is important to get real time data from the field. Therefore, an attempt was made to collect data from various sources to study the impact of IBR penetration on protective relaying. Analysis done on the sample cases from Indian grid has been presented in the following paragraphs.

Table 4 Directional relay behaviour summary from literature survey

| Type of fault | Fault location | Type | Relay R1 Computation method |  |  | Relay R2 Computation Method |  |  | Ref. | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Positive Seq | Negative Seq | Zero Seq | Positive Seq | Negative Seq | Zero Seq |  |  |
| SLG | F1 | Conv. | Fw | Fw | Fw | Fw | Fw | Fw | [10] [11] [22] |  |
|  | F1 | IBR | Fw | N.D | On Margin | Fw | N.D | On Margin | [3] [14] [15] [21] [24] | For R1 - Positive Sequence takes 3 cycle to settle |
| DLG | F1 | Conv. | Fw | Fw | Fw | Fw | Fw | Fw | [10] [22] |  |
|  | F1 | IBR | Fw | Fw | On Margin | Fw | N. D | On Margin | [3] [14] [15] [21] [24] |  |
| 3LG | F1 | Conv. | Fw | Fw | Fw | Fw | Fw | Fw | [10] [22] |  |
|  | F1 | IBR | Fw | N.D | N.D | Fw | N.D | N.D | [3] [14] [15] [21] [24] |  |
| SLG | F2 | Conv. | Rev | Rev | Rev | Fw | Fw | Fw | [22] |  |
|  | F2 | IBR | Rev | N.D | On Margin | Fw | N.D | On Margin | [3] [14] [15] [21] [24] | For R2 - Positive Sequence takes 1 cycle to settle |
| DLG | F2 | Conv. | Rev | Rev | Rev | Fw | Fw | Fw | [22] |  |
|  | F2 | IBR | Rev | N.D | On Margin | Fw | N.D | On Margin | [3] [14] [15] [21] [24] |  |
| 3LG | F2 | Conv. | Rev | Rev | Rev | Fw | Fw | Fw | [24] |  |
|  | F2 | IBR | Rev | N.D | N.D | Fw | N.D | N.D | [3] [14] [15] [21] [24] |  |
| Note 1: 1. SLG - single line to ground fault 2. DLG - double line to ground fault 3. 3LG - three Phase to ground fault |  |  |  | Note 2: 1. Conv. – Conventional sources on both sides 2. IBR - one side with conventional and other side with IBR 3. Fw - Forward direction fault 4. Rev - Fault in Reverse direction 5. N.D – Not detected 6. On Margin - Fault detected, on the boundary of the margin |  |  |  |  |  |  |

As a first step, the disturbance report gathered was analysed to understand the type of fault, behaviour of the relays before the fault, during the fault and after the fault specially to isolate the fault. Later, the fundamental voltage and current phasors were computed from the available data using full cycle window fourier algorithm, the most popularly used technique in the modern relays [40]. These data were used to compute the impedance phasor and sequence components. The line parameters available were used to derive the compensating factors necessary during the computation [41]. Though various impedance characteristics are possible to set in a typical line protection relay, for the cases considered in the field study, a typical characteristic from Hitachi REL 670 has been considered [38] , [42] . The impedance angle was passed through the directionality criteria check program to observe the behaviour of the element during various fault conditions. The check program is verifying condition when the impedance angle is within the boundary of directionality i.e between -15 degrees and +115 degrees [38] , [42]. The criteria against the impedance angle is computed at each sample and is plotted specially during fault duration with

- Logic 0 directional condition not met

- Logic 1 directional condition met

The observations for each field case have been summarized in Table 5 and performance evaluation against relay logic scheme are presented in the subsequent section.

Table 5 Summary of observations from the field cases

| Type of DER | Type of Fault | Grid End | DER End | Remarks |
| --- | --- | --- | --- | --- |
| Type-4 | Phase to Ground | - Current lags voltage in the faulty phase by 84 degrees | - Current is in-phase during pre-fault and fault conditions - During the initial few cycles of fault, current behavior is different compared to steady state. - Voltage magnitude both in DER end and Grid end are same during 3 cycles of fault on healthy phase - No neutral current was observed, we observe a residual voltage, 3U0 | - Can be segregated as Pseudo-physical period and inverter control period. |
| Solar | Two phase to Ground | - Current lags voltage in the faulty phase by 27 degrees | - Voltage reduced in the faulty phases - Current goes to value 0 | - NA |
| Type-3 | Phase to Ground | - Current lags voltage in the faulty phase by 76 degrees | - Current reduction seen in faulty phase only unlike Type 4 and voltage reduction also seen in faulty phase. - Current lags voltage in faulty phase by 56 deg during fault (in phase during pre-fault close to 7 deg) - Current magnitude changed to 80%, but not still reaching rated value | - Current reduction seen in faulty phase only and current wave form is close to conventional unlike in Type 4 where it is different after 2 cycle |

  - Field case-1: Type-4 Wind Farm:

Disturbance Report collected from fault in 125 kV line connected to wind farm Type-4 was made available, with fault on protection line with one end Grid and other end Type-4 wind generation as DER.

Fig.5. Single Line Diagram Type-4 Wind Power Plant

The single line diagram is shown in Fig.5.We observe that there is a single phase to ground fault and is in B phase. Fault waveforms both in Grid end and DER end for the faulty phases are shown in Fig.6 and Fig.7. The pre-fault waveform in Fig.6 shows balanced condition. At Grid end, during fault, the B phase current has increased almost 10 times pre fault value and voltage has reduced drastically.  On the DER end during pre-fault we see balanced condition, and during fault, voltage is also reduced as in Fig.7.

However, no neutral current or zero-sequence current was observed. Current is further observed to have increased in both A Phase and B phase. When impedance was computed for phase to neutral, B phase directionality criteria is met at Grid end as in Fig.8. The check program is used to verify this condition. At DER end behaviour is different and directionality/ zone reach criteria is not met. The phaser diagrams on both the ends confirm this behaviour as in Fig.9 and Fig.11 for pre-fault condition, and Fig.10 and Fig.12 for during fault condition. The line parameter considered are as in Table 6 of Appendix.

Voltage (V)

Current (A)

Time (s)

Time (s)

Fig.6. Type-4 Wind: LG Fault Grid End waveform

Voltage (V)

Current (A)

Time (s)

Time (s)

Fig.7. Type-4 Wind: LG Fault DER End waveform

Fig.8. Type-4 Wind: LG Fault Faulty phase Impedance Trajectory (a) Grid end (b) DER end

DER end

Resistance (Ω)

Reactance (Ω)

-10

-20

-30

-40

-80

-60

-40

-20

0

10

20

30

40

10

20

30

40

0

Resistance (Ω)

-10

-20

-30

-40

10

20

30

-80

-60

-40

-20

0

10

20

30

40

Reactance (Ω)

0

a)

b)

Fig.9. Type-4 Wind: LG Fault Grid end pre-fault phaser (a) Current (b) Voltage

Current

Voltage

A Phase

B Phase

C Phase

a)

b)

Fig.10. Type-4 Wind: LG Fault Grid end during fault phaser (a) Current (b) Voltage

during fault

Current

Voltage

A Phase

B Phase

C Phase

Fig.11. Type-4 Wind: LG Fault DER end pre-fault phaser (a) Current (b) Voltage

Current

Voltage

A Phase

B Phase

C Phase

Fig.12. Type-4 Wind: LG Fault DER end during fault phaser (a) Current (b) Voltage

Current

Voltage

A Phase

B Phase

C Phase

a)

b)

  - Field case-2: Solar Plant:

Another disturbance report from 220 kV line connected to a solar park in western grid was made available.  The SLD is shown in Fig.13. During pre-fault condition, system is normal with both phase B and C phase voltage and current waveform in Fig.14 and Fig.15.

Fig.13. SLD for Grid connected solar power plant

There was a LLG fault and from the disturbance record, we could observe that it is a fault in B and C Phase at the 500 ms from the time of DR capture, at Grid end as in Fig.14. At DER end, there is no current feed from solar side and phase voltage collapse from 120 kV to 6 kV as in Fig.15 at the 900 ms from the time of DR capture.

The angle shift of 20 degrees between healthy phase voltage and current and 40 degrees between faulty phase voltage and currents also could be seen in the disturbance report as in Fig.16. This is not typical to conventional system and continues to be resistive in nature and is showing export behaviour.

Phase B Voltage (V)

Phase C Voltage (V)

Phase B Current (A)

Time (s)

Phase C Current (A)

Time (s)

Time (s)

Fig.14. Solar Plant: LLG Fault: Grid end fault waveform (a) Phase B (b) Phase C

Time (s)

a)

b)

Phase B Voltage (V)

Phase C Voltage (V)

Phase B Current (A)

Time (s)

Phase C Current (A)

Time (s)

Time (s)

Fig.15. Solar Plant: LLG Fault: DER end fault waveform (a) Phase B (b) Phase C

Time (s)

When the impedance trajectory was used to check the directionality criteria, we could observe that for B Phase and C Phase (LL fault) criteria was met at Grid end as can be seen in Fig.16 and at DER end it was oscillating.  The phasor diagrams on both the ends confirm this behaviour as in Fig.17 and Fig.19 for pre-fault condition, Fig.18 and Fig.20 for during fault condition.

Resistance (Ω)

Resistance (Ω)

Reactance (Ω)

10

0

20

30

40

-10

-20

-30

-40

0

-80

-60

-40

-20

20

40

60

80

40

Reactance (Ω)

0

10

20

30

-10

-20

-30

-40

-80

-60

-40

-20

0

20

40

60

80

Fig.16. Solar Plant: LLG Fault Faulty phase Impedance Trajectory (a) Grid end (b) DER end

Fig.17. Solar Plant: LLG Fault Grid end pre-fault phaser (a) Current (b) Voltage

Voltage

hasor diagram Grid End pre-fault

A Phase

B Phase

C Phase

Current

Voltage

a)

b)

Fig.18. Solar Plant: LLG Fault Grid end during fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

Fig.19. Solar Plant: LLG Fault DER end pre-fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

Fig.20. Solar Plant: LLG Fault DER end during fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

- Field case-3: Type-3 Wind Farm:

The Disturbance report from 220KV single circuit line connected to Type-3 wind farm was made available. The SLD for the plant is shown in Fig.21. It was a LG fault on A phase. The disturbance report shows during pre-fault the system is balanced and current direction is reverse with an angle of close to 173 degrees lag. Power flow direction before fault at Grid end is reverse and at DER end is forward. During fault, current raised in faulty phase significantly as in Fig.22 and Fig.23 though drop in voltage not quite big.

Fig.21. SLD for Type-3 Wind Farm

If we observe the changes in current magnitude, we can infer that at Grid end, during pre-fault the current was around 25% of rated value whereas 360ms earlier to the fault it rose up to 2.5 times rated current and remained same till the fault instant. We also observed that other 2 phase current magnitudes went close to 50% of rated value. The current at DER end started changing around 80ms earlier to the fault and it rose and didn’t reach rated value, but started declining soon.

During fault, Grid side directionality is still ascertained though the angle is 76 degrees lag, however due to the impedance angle which goes outside the boundary, relay fails to ascertain directionality on the DER end as seen in Fig.23. When the impedance trajectory was used to check the directionality criteria, we could observe that for A phase, fault criteria was met at Grid end as can be seen in Fig.24 and also at DER end. The phasor diagrams on both the ends confirm this behaviour as in Fig.25 and Fig.27 for pre-fault condition, Fig.26 and Fig.28 for during fault condition. The line parameters used are as in Table 8 of Appendix.

368 A

(pre-fault)

3277A (during fault)

Current (A)

Time (s)

Time (s)

Voltage (V)

132 kV (pre-fault)

119 kV (during fault)

Fig.22. Type-3 Wind: LG Fault: Grid end waveform (a) Current (b) Voltage

Voltage (V)

132 kV (pre-fault)

8kV (during fault)

Time (s)

Fig.23. Type-3 Wind: LG Fault: DER end waveform (a) Voltage (b) Current

Time (s)

Current (A)

371 A (pre-fault)

1053A (during fault)

Resistance (Ω)

Resistance (Ω)

Reactance (Ω)

Reactance (Ω)

10

0

20

30

40

-10

-20

-30

-40

0

-80

-60

-40

-20

20

40

60

80

0

10

20

30

40

-10

-20

-30

-40

-80

-60

-40

-20

0

20

40

60

80

Fig.24. Type-3 Wind: LG Fault Faulty phase Impedance Trajectory (a) Grid end (b) DER end

end)

Fig.25. Type-3 Wind: LG Fault Grid end pre-fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

Fig.26. Type-3 Wind: LG Fault Grid end during fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

Fig.27. Type-3 Wind: LG Fault DER end pre-fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

Fig.28. Type-3 Wind: LG Fault DER end during fault phaser (a) Current (b) Voltage

A Phase

B Phase

C Phase

Current

Voltage

Discussions:

The response of the system for field cases with different faults and when system has different sources are shown in Table 5. The response for each type of fault varies for different sources in the system. When line is terminated to Grid or has a DER source the current magnitude and angle vary due to the influence of inverter characteristics. Significant reduction in the magnitude of current is observed from DER.

In case of Type–3 wind, the voltage reduction happened in faulty phase alone and current waveform is close to conventional. In Type-4 it is different after 2 cycles. In the Type–4 case it can be segregated as Pseudo-physical period and inverter control period when the inverter actions are seen to be effective. The current angle which was lagging by 48 degrees with respect to B phase voltage during the pseudo -physical period has changed to 17 degrees lag during the post pseudo-physical period as shown in Fig.29 and Fig.30 respectively.

Pseudo-physical period

Current Angle

Fig.29. Type-4 Wind: Pre-fault current and voltage angle

The impedance trajectory also shows the same behaviour as in Fig.31 and Fig.32.

Trajectory outside

Inverter control period

Current Angle

Fig.30. Type-4 Wind: During fault current and voltage angle

Resistance (Ω)

40

Reactance (Ω)

0

10

20

30

-10

-20

-30

-40

0

-80

-60

-40

-20

20

40

60

80

Reactance (Ω)

Resistance (Ω)

0

50

100

150

200

-50

-100

-150

-200

-400

-300

-200

-100

0

100

200

300

400

500

Fig.31. Type-4 Wind: Pseudo-physical period impedance trajectory

Resistance (Ω)

Reactance (Ω)

0

10

20

30

40

-10

-20

-30

-40

0

-20

-40

-60

-80

20

40

60

80

Reactance (Ω)

Resistance (Ω)

0

10

20

30

40

-10

-20

-30

-40

-100

-60

-20

0

20

60

100

Trajectory inside

Fig.32. Type-4 Wind: Inverter control period impedance trajectory

For Type–4 wind, the behaviour with sequence component methods were investigated and the positive sequence method results were same as with fundamental method both in Grid end and DER end. However, both negative sequence and zero sequence based methods fail to conclude on the directionality criteria at both ends as indicated in Fig.33 and Fig.34. The check program is used to evaluate the condition of angle within the boundary of directionality i.e., between -15 degrees and +115 degrees.

The criteria was met with zero sequence computation method at Grid end. However, at DER end, it is quite uncertain and not consistent as seen in Fig.34.

(a)

(b)

(c)

Fault instance

Directionality criteria

Sample number

Sample number

Sample number

Fig.33. Type-4 Wind: Sequence component directionality check at Grid end (a) Positive (b) Negative (c) Zero

Directionality not detected

Directionality not detected

Directionality detected

For solar case positive sequence method works. However, negative sequence and zero sequence methods fail to detect directionality as in Fig.35 and Fig.36. At Grid end, if the protection algorithm can measure during initial few milliseconds, it might be able to detect directionality as seen in Fig.35. However, in zero sequence computation response is uncertain.

(a)

(c)

Directionality detected after fault clearance

Sample number

Sample number

Sample number

(b)

Directionality criteria

Directionality not detected

Directionality detected

Directionality

not detected

Fault instance

Fig.34. Type-4 Wind: Sequence component directionality check at DER end (a) Positive (b) Negative (c) Zero

(c)

Directionality criteria

Sample number

Sample number

Sample number

(a)

(b)

Fault instance

Directionality not detected

Directionality detected

Directionality not detected

Directionality detected after fault clearance

Fig.35.Solar: Sequence component directionality check at Grid end (a) Positive (b) Negative (c) Zero

(c)

Directionality detected

Directionality on-margin

Directionality criteria

Sample number

Sample number

Sample number

(a)

(b)

Directionality detected after fault clearance

Fault instance

Fig.36. Solar: Sequence component directionality check at DER end (a) Positive (b) Negative (c) Zero

At DER end, with positive sequence method results were same as at Grid end. However, both negative sequence and zero sequence methods fail to conclude on the directionality criteria as indicated in Fig.36.

The same was evaluated also for Type–3 wind case and similar behaviour was observed where positive sequence computation works, but negative sequence and zero sequence methods fail to conclude as seen in Fig.37 and Fig.38.Additional two computations of directionality check were performed with in feed from the DER end being 10% and 20% of the full load current. There is no impact with this as shown in example for Type-3 wind resource as could be seen in Fig.39, Fig.40, and Fig.41. The study is based on the availability of field data. More cases of different types of faults need to be further taken up. Further dedicated study on mechanisms of inverter control and its impact on each type of fault on directionality check could provide more insight into possible ways how the mal operations could be contained. During fault, Type 4 wind and solar systems have similar response characteristics.

(c)

Directionality detected

Directionality criteria

Sample number

Sample number

Sample number

(a)

(b)

Directionality on-margin

Directionality not detected

Fault instance

Fig.37. Type-3 wind: Sequence component directionality check at Grid end (a) Positive (b) Negative (c) Zero

Sample number

Sample number

Sample number

(a)

(b)

(c)

Directionality criteria

Fault instance

Directionality not detected

Directionality not detected

Directionality not detected

Fig.38. Type-3 wind: Sequence component directionality check at DER end (a) Positive (b) Negative (c) Zero

Directionality criteria

Directionality detected

Sample number

Sample number

Sample number

Sample number

(a)

(b)

(c)

(d)

Directionality not detected

Directionality not detected

Fault instance

Directionality detected

Fig.39. Type-3 wind: impact of DER infeed on positive sequence method (a) Grid side with 10% DER infeed (b) DER side with 10% DER infeed (c) Grid side with 20% DER infeed (d) DER side with 20% DER infeed

Directionality criteria

(d)

Sample number

Sample number

Sample number

Sample number

(a)

(b)

(c)

Fault instance

Directionality not detected

Directionality not detected

Directionality not detected

Directionality detected after fault clearance

Fig.40. Type-3 wind: impact of DER infeed on negative sequence method (a) Grid side with 10% DER infeed (b) DER side with 10% DER infeed (c) Grid side with 20% DER infeed (d) DER side with 20% DER infeed

Directionality criteria

Sample number

Sample number

Sample number

Sample number

(a)

(b)

(c)

(d)

Directionality not detected

Directionality not detected

Directionality not detected

Directionality not detected

Fig.41. Type-3 wind: impact of DER infeed on zero sequence method (a) Grid side with 10% DER infeed (b) DER side with 10% DER infeed (c) Grid side with 20% DER infeed (d) DER side with 20% DER infeed

Fault instance

Conclusions:

From the field records following generalization could be arrived at:

- Detection based on sequence components must be completed within a maximum time of 5 ms from the fault inception. This will ensure detection for any kind of source (Solar, Type–3, and Type–4)

- The phasor information post 40 ms from the fault inception is purely inverter control driven and not system based, thus not only directionality would be affected even other functions like distance protection, overcurrent protection, earth fault will be affected as well.

  - For distance protection the impedance locus may enter the load encroachment area, thus not detecting the fault zone.

  - For overcurrent and earth fault, relay will not operate since the angle between voltage and current will be outside the relay operate angle region (ROA)

- Contrary to work proposed by authors [20] to have directional relays on both ends, will not ensure detection and isolation of the fault since the operate region is not ascertained by directional relay.

- Conventional time delayed back up protection such as delayed overcurrent/ earth fault, Z-2/ Z-3 protection will not operate reliably.

- Only unit protection such as differential protection will operate reliably in the phasor-based algorithms.

Lots of studies have been done on the impact of inverter-based resource penetration to power system in various countries. The relay algorithms either need modifications to rightly detect the direction of fault, or necessary corrections could be made by deploying adaptive dynamic methods.

Appendix

The line parameters for various cases are as per the table below:

Table 6 Line Parameters (Type-4 Wind)

| Parameter | Details | Value in Ohm/phase/km |
| --- | --- | --- |
| Positive sequence | R1L | 0.0581 |
|  | X1L | 0.392 |
| Zero sequence | R0L | 0.254 |
|  | X0L | 1.1044 |

Table 7 Line Parameters (Solar)

| Parameter | Details | Value in Ohm/phase/km |
| --- | --- | --- |
| A-Phase | R1A | 0.28 |
|  | X1A | 3.16 |
| B-Phase | R1B | 0.28 |
|  | X1B | 3.16 |
| Positive sequence | R1L | 0.83 |
|  | X1L | 4.19 |
| Zero sequence | R0L | 2.31 |
|  | X0L | 14.06 |

Table 8 Line Parameters (Type-3 Wind)

| Parameter | Details | Value in Ohm/phase/km |
| --- | --- | --- |
| Positive sequence | R1L | 0.0581 |
|  | X1L | 0.392 |
| Zero sequence | R0L | 0.254 |
|  | X0L | 1.1044 |

REFERENCES

- McKinsey & Company. (April 2022). Global Energy Perspective 2022 Executive Summary. McKinsey & Company

- Eto, Joseph & Lasseter, R.H. & Klapp, David & Khalsa, Amrit & Schenkman, Benjamin & Illindala, Mahesh & Baktiono, Surya. (2018). The CERTS Microgrid Concept, as Demonstrated at the CERTS/AEP Microgrid Test Bed.

- A. Haddadi, E. Farantatos, I. Kocar, and U. Karaagac, “Impact of Inverter Based Resources on System Protection,” Energies 2021, 14,1050. https://doi.org/10.3390/en14041050

- NERC. (2015). Analysis of System Protection Misoperations. Atlanta: NERC. [online]Available: https://nerc.com/pa/rapa/pa/performance%20analysis%20dl/2015_analysis_of_system_protection_misoperations_final.pdf

- WECC. (2017). Protection System Misoperations Report and Mitigation Approaches. WECC. [online] Available https://www.wecc.org/Reliability/2017_ProtectionSystemMisoperations_Report.pdf

- Sticht, C. (2021). Investigation of Misoperations on the North American BPS. OAK RIDGE NATIONAL LABORATORY for US Department of Energy. [online] Available: https://www.osti.gov/servlets/purl/1836418

- CSTEP. (2021). Grid impact for High RE scenarios for Southern India by Center for Study of Science, Technology and Policy (CSTEP), January 2021 Center for Study of Science, Technology and Policy (CSTEP).

- SRLDC, R. (2021). Renewable energy in southern region – Journey so far. REMC, SRLDC, POSOCO. [online] Available: https://www.srldc.in/UploadFiles/NewsAndUpdate/RenewableEnergyInSouthernRegion%20-%20JourneySoFar01122021.pdf

- R. M. Elavarasan et al., "A Comprehensive Review on Renewable Energy Development, Challenges, and Policies of Leading Indian States with an International Perspective," in IEEE Access, vol. 8, pp. 74432-74457, Apr. 2020.

- J. Horak, "Directional overcurrent relaying (67) concepts," 59th Annual Conference for Protective Relay Engineers, 2006., College Station, TX, USA, 2006, pp. 13 pp.-, doi: 10.1109/CPRE.2006.1638701.

- J.Roberts, and A. Guzman, “Directional element design and evaluation,” 2006. [Online]. Available: https://cdn.selinc.com/assets/Literature/Publications/Technical%20Paper /6009 Directional Element JBR-AG 20060803 Web.pdf.

- K. Zimmerman and D. Costello, "Fundamentals and improvements for directional relays," 2010 63rd Annual Conference for Protective Relay Engineers, College Station, TX, USA, 2010, pp. 1-12, doi: 10.1109/CPRE.2010.5469483.

- A. Hooshyar, M. A. Azzouz and E. F. El-Saadany, "Distance Protection of Lines Connected to Induction Generator-Based Wind Farms During Balanced Faults," in IEEE Transactions on Sustainable Energy, vol. 5, no. 4, pp. 1193-1203, Oct. 2014, doi: 10.1109/TSTE.2014.2336773.

- A. Roy and B. K. Johnson, "Transmission side protection performance with Type-IV wind turbine system integration," 2014 North American Power Symposium (NAPS), Pullman, WA, USA, 2014, pp. 1-6, doi: 10.1109/NAPS.2014.6965429.

- Chen, A. Shrestha, F. A. Ituzaro and N. Fischer, "Addressing protection challenges associated with Type 3 and Type 4 wind turbine generators," 2015 68th Annual Conference for Protective Relay Engineers, College Station, TX, USA, 2015, pp. 335-344, doi: 10.1109/CPRE.2015.7102177.

- V. Telukunta, J. Pradhan, A. Agrawal, M. Singh and S. G. Srivani, "Protection challenges under bulk penetration of renewable energy resources in power systems: A review," in CSEE Journal of Power and Energy Systems, vol. 3, no. 4, pp. 365-379, Dec. 2017, doi: 10.17775/CSEEJPES.2017.00030.

- H. Jafarabadi Ashtiani, H. Samet, and T. Ghanbari, “Evaluation of directional relay algorithms in the presence of FCL,” IET Sci., Meas. Technol., vol. 11, no. 6, pp. 713–722, Sep. 2017.

- S. K. Al-Sachit, M. J. Sanjari and N. -K. C. Nair, "Negative Sequence-Based Schemes for Power System Protection - Review and Challenges," 2018 Australasian Universities Power Engineering Conference (AUPEC), Auckland, New Zealand, 2018, pp. 1-6, doi: 10.1109/AUPEC.2018.8758012.

- J. Han, L. Zheng, K. Jia, Y. Fang, Z. Yang and R. Chen, "Protection adaptability analysis in VSC-HVDC-connected offshore wind farm system," 8th Renewable Power Generation Conference (RPG 2019), Shanghai, China, 2019, pp. 1-5, doi: 10.1049/cp.2019.0311.

- M. Nagpal and C. Henville, "Impact of Power-Electronic Sources on Transmission Line Ground Fault Protection," in IEEE Transactions on Power Delivery, vol. 33, no. 1, pp. 62-70, Feb. 2018, doi: 10.1109/TPWRD.2017.2709279.

- IEEE PES. (2020). Technical report PES-TR-81: Protection Challenges and Practices for Interconnecting Inverter Based Resources to Utility Transmission Systems. IEEE Power & Energy Society.

- P. Adhikari, S. Brahma and P. H. Gadde, "Addressing the Performance of Distance Relays in Presence of Inverter Based Resources," 2021 North American Power Symposium (NAPS), College Station, TX, USA, 2021, pp. 1-6, doi: 10.1109/NAPS52732.2021.9654441.

- V. Pradhan, N. George, O. D. Naidu, Z. Gajic and S. Zubic, "Distance protection of inverter-based renewables power evacuating lines and downstream network: Issues and mitigation approach," 2022 IEEE PES Innovative Smart Grid Technologies - Asia (ISGT Asia), Singapore, Singapore, 2022, pp. 215-219, doi: 10.1109/ISGTAsia54193.2022.10003580.

- A. V, O. D. Naidu and M. N. Alam, "Assessment of Directional Elements for Power Networks Connected to Inverted Based Renewable Resources: Problems and Mitigation Approach," 2023 IEEE PES GTD International Conference and Exposition (GTD), Istanbul, Turkiye, 2023, pp. 371-375, doi: 10.1109/GTD49768.2023.00097.

- "Fault current contributions from wind plants," 2015 68th Annual Conference for Protective Relay Engineers, College Station, TX, USA, 2015, pp. 137-227, doi: 10.1109/CPRE.2015.7102165.

- A. Haddadi, M. Zhao, I. Kocar, U. Karaagac, K. W. Chan and E. Farantatos, "Impact of Inverter-Based Resources on Negative Sequence Quantities-Based Protection Elements," in IEEE Transactions on Power Delivery, vol. 36, no. 1, pp. 289-298, Feb. 2021, doi: 10.1109/TPWRD.2020.2978075.

- A. Haddadi, I. Kocar, J. Mahseredjian et al., “Negative sequence quantities-based protection under inverter-based resources – challenges and impact of the German grid code”, in Proceedings of 21st Power Systems Computation Conference, Porto, Portugal, Jun. 2020, pp. 1-12.

- R. Chowdhury and N. Fischer, "Transmission Line Protection for Systems with Inverter-Based Resources – Part II: Solutions," in IEEE Transactions on Power Delivery, vol. 36, no. 4, pp. 2426-2433, Aug. 2021, doi: 10.1109/TPWRD.2020.3030168.

- G. Kou, J. Jordan, B. Cockerham, R. Patterson and P. VanSant, "Negative-Sequence Current Injection of Transmission Solar Farms," in IEEE Transactions on Power Delivery, vol. 35, no. 6, pp. 2740-2743, Dec. 2020, doi:10.1109/TPWRD.2020.3014783.

- R. Chowdhury and N. Fischer, "Transmission Line Protection for Systems with Inverter-Based Resources – Part I: Problems," in IEEE Transactions on Power Delivery, vol. 36, no. 4, pp. 2416-2425, Aug. 2021, doi: 10.1109/TPWRD.2020.3019990.

- D. Kelly, P. Mysore and N. Mohan, "A Novel Control Scheme for Utility-Scale Inverter-Based Resources to Emulate Synchronous Generator Fault Response and Retain Existing Protection Infrastructure," 2021 74th Conference for Protective Relay Engineers (CPRE), College Station, TX, USA, 2021, pp. 1-7, doi: 10.1109/CPRE48231.2021.9429836.

- W. Liu, Q. Tu, Y. Lv, G. Song, X. Gao and P. Chang, "The Adaptability Analysis of the Traditional Protections in Offshore Wind Power System," 2022 China International Conference on Electricity Distribution (CICED), Changsha, China, 2022, pp. 1554-1560, doi: 10.1109/CICED56215.2022.9928815.

- B Martínez Carrasco, E.; Comech Moreno, M.P.; Villén Martínez, M.T.; Borroy Vicente, S. “Improved Faulted Phase Selection Algorithm for Distance Protection under High Penetration of Renewable Energies,” Energies 2020, 13, 558.https://doi.org/10.3390/.

- A. A. Aboelnaga, M. A. Azzouz, H. F. Sindi and A. S. A. Awad, "Fault Ride Through of Inverter-Interfaced Renewable Energy Sources for Enhanced Resiliency and Grid Code Compliance," in IEEE Transactions on Sustainable Energy, vol. 13, no. 4, pp. 2275-2290, Oct. 2022, doi: 10.1109/TSTE.2022.3191631.

- Quispe, J.C., Orduña, E. “Transmission line protection challenges influenced by inverter-based resources: a review”, Prot Control Mod Power Syst 7, 28 (2022). https://doi.org/10.1186/s41601-022-00249-8

- Binni, M., Abboud, R., Lima, P., & Lollo, F. (2021). Challenges and Solutions in the Protection of Transmission Lines Connecting Nonconventional Power Sources. 48th Annual Western Protective Relay Conference, October 2021.

- Application manual, Line distance protection REL 670.2” [Online]. Available: https://library.e.abb.com/public/8c1eb95cc50243c4c1257d9300423926/1MRK506338-UUS_-_en_Application_manual__Line_distance_protection_REL670_2.0__ANSI.pdf. Accessed on 31st May 2023.

- Hitachi Energy Line Distance Protection REL670 Manual, [online] Available: https://search.abb.com/library/Download.aspx?DocumentID=1MRK506372-BEN&LanguageCode=en&DocumentPartId=&Action=Launch.

- IEEE/NERC Task Force on Short-Circuit and System Performance Impact of Inverter Based Generation. (2018). Technical Report: PES-TR68: Impact of Inverter Based Generation on Bulk Power System Dynamics and Short-Circuit Performance. IEEE PES. . [online] Available: https://resourcecenter.ieee-pes.org/publications/technical-reports/pes_tr_7-18_0068

- Yuansheng Liang, Jiayan Ding, Haifeng Li, Gang Wang, Zihong Zhang, “Transmission line frequency-domain fault location method based on the phasor-time space curve characteristics that considers decaying DC deviation”, International Journal of Electrical Power & Energy Systems, Volume 142, Part B,2022,108308,ISSN

- VERZOSA, Q., & Jun, J. (n.d.). Ground Distance Relays – Understanding the Various Methods of Residual Compensation, Setting the Resistive Reach of Polygon Characteristics, and Ways of Modeling and Testing the Relay. Doble Engineering company [online]. Retrieved from https://na.eventscloud.com/file_uploads/bb8b9912d1cf853b07957eff1965fb3f_GroundDistanceRelays-ResidualCompensation.pdf

- "IEEE Guide for Protective Relay Applications to Transmission Lines," in IEEE Std C37.113-2015 (Revision of IEEE Std C37.113-1999), vol., no., pp.1-141, 30 June 2016, doi: 10.1109/IEEESTD.2016.7502047