An Adaptive Distance Protection Scheme Considering Fault Resistance, Injected Current, and Structural Changes in the Power System

Majid Mohtashami1, Abbas Saberi Noghabi2

1 Faculty of Electrical and Computer Engineering – University of Birjand - Birjand - Iran majidmohtashami@birjand.ac.ir

2 Faculty of Electrical and Computer Engineering – University of Birjand - Birjand – Iran a.saberi@birjand.ac.ir

Abstract:

Faults in power systems occur for various reasons, such as aging or natural disasters. Detecting, locating, and promptly clearing these faults is crucial for maintaining the safety and reliability of transmission lines. Distance relays, which protect transmission lines, detect faults, estimate their location, and send the required commands. However, these relays may experience mis-detection due to manipulated impedance arising from both internal and external factors. These factors include measurement device errors, network topology changes, the presence of fault resistance, and injected currents from remote line terminals. To address this challenge, we propose an innovative adaptive protection scheme that considers fault resistance, changes in network topology, and injected current from the opposite end of the line. By estimating the equivalent circuit impedances of the network connected to the terminal of the transmission line, this protection scheme utilizes impedance estimation techniques at the line terminals and offline network information. Simulation studies (tested on the IEEE 39-bus standard network) show that the proposed scheme accurately estimates fault location and fault resistance with high precision. The simulation results demonstrate its effectiveness in improving the performance of conventional distance protection relays in both the first and second protection zones (Z1 and Z2).

Keywords:

Adaptive Protection Scheme, Distance Relay, Fault Location, Network Structure Change, thevenin Equivalent Impedance, Fault Resistance, Network Equivalent Circuit.

Introduction:

In the present era, with the ever-expanding demand for electrical energy, power transmission networks have been developed across vast geographical areas. On the other hand, the importance of continuous and high-quality electricity supply has led energy providers to continuously improve the performance of their network protection systems and reduce the downtime for faulted sections. Accurately identifying the location and resistance of faults in power transmission networks to speed up network recovery is a major challenge. This problem is particularly significant given the large scale of current networks and the occasional difficulties in accessing the routes of transmission lines. (Igberaese et al., 2023; Panahi et al., 2021).

The philosophy of distance protection, which serves as the primary protection for transmission networks, relies on estimating the distance to the fault location from the relay installation point using the calculated impedance (Horowitz et al., 2022). Multiple factors contribute to distance relay errors in estimating the fault location (Igberaese et al., 2023; Nikolaidis et al., 2018; Saha et al., 2010). In the event of a fault, three influential factors affecting the impedance calculated by the distance relay are network topology uncertainty, fault resistance magnitude, and injected current from the other end of the transmission line at the fault location. These factors can lead to either overreach or underreach relay errors (Eriksson et al., 1985; Saha et al., 2010; Takagi et al., 1982). Nowadays, due to the widespread adoption of digital relays in power transmission systems, more complex protection algorithms have become feasible (Anderson et al., 2022). Distance protection algorithms are continuously evolving to adapt to various network conditions (Igberaese et al., 2023). The adaptability’s effectiveness is demonstrated when online adjustments are made to protection characteristics or configurations, taking into account various operational situations and conditions. It should be capable of reducing or eliminating relay errors (Nikolaidis et al., 2018; Sarangi et al., 2021). In this study, a novel adaptive protection scheme for distance relays is introduced to mitigate the adverse effects of three uncertainty factors: network configuration changes, fault resistance, and injected current from the remote end of the transmission line. This protective scheme relies on modeling the network connected to the terminals of the transmission line and online estimating equivalent circuit impedances. It enhances the performance of distance relays in both Zone 1 and Zone 2 by utilizing local information during fault events and data from the remote end of the transmission line. Furthermore, in case of a fault on the transmission line, it can precisely estimate the fault location and fault resistance online. In this proposed scheme, to estimate the equivalent circuit parameters of the network from the viewpoint of transmission line terminals, it is necessary to examine various configurations of the network connected to the transmission line (and classify them, if needed) in order to create a relay database. Then, using this information and online estimation of the network’s thevenin impedance at the transmission line terminals, the equivalent circuit parameters of the existing configuration will be determined. Finally, in the event of a fault, precise fault resistance and location can be determined with high accuracy using information from the pure faulted (superimposed) network, aided by the estimated equivalent circuit.

In this study, the model used for the transmission line network is a comprehensive model based on the work of (Anderson et al., 2022; Eisa & Ramar, 2010; Wiszniewski, 1983). The significant innovation lies in the online estimation of all the equivalent circuit impedances. Therefore, the proposed model has the capability to adapt online to various network configurations. Additionally, the proposed algorithm can accurately estimate the fault resistance and location independently of the fault resistance value and the injected current from the remote end of the transmission line.

Adaptive Distance Protection

Adaptive protection refers to a concept where protective relays need to adjust their operational characteristics to match the power system conditions (Horowitz et al., 2022). The proposed adaptive protection scheme is based on fault loop calculations and equivalent impedances of the network under pure fault (superimposed network) conditions.

History

In 1982, Takagi and colleagues proposed the separation of the network under pure fault conditions from the faulty network by simplifying fault loop equations. They introduced an algorithm to determine fault location based on single-end data of line terminals (Takagi et al., 1982). A year later, in (Schweitzer III, 1983), an algorithm for improving the accuracy of the Takagi method (presented in (Takagi et al., 1982)) was introduced, which required data from both ends of the transmission line. Simultaneously, in (Wiszniewski, 1983), an accurate fault location algorithm was introduced for locating faults from a single end. This method utilizing the complete model of a transmission line within an interconnected network and is specifically designed to identify single-phase-to-ground and phase-to-phase faults. In 1985, Eriksson et al.  simplified the model used in (Wiszniewski, 1983) and proposed the use of positive, negative, and zero sequence networks and by separating the pure-fault network from the faulty network and utilizing data from both line terminals, the concept of current distribution coefficients was introduced. Based on this, a novel fault location method was proposed that exhibited high accuracy in Interregional transmission lines. Although the mentioned methods are easily implementable in modern digital relays, it was in (Cook, 1986) that three different algorithms were first introduced for use in distance relays. The two-terminal location determination method presented in (Johns & Jamali, 1990) utilized distributed parameters model for the faulted transmission line and did not depend on the fault resistance. In (Novosel et al., 1996), a two-terminal offline fault location method was proposed that did not require synchronized information. In (Izykowski et al., 2004), a single-terminal fault location method used in parallel transmission lines was introduced. In 2010, (Eisa & Ramar, 2010) presented a single-terminal fault location method for all types of transmission line faults, using a comprehensive network model and distributed parameters model for the faulted transmission line. In 2017, an adaptive protection scheme for distance relays was proposed in (Paladhi & Pradhan, 2017), considering the effect of network configuration changes and providing a different formulation based on network impedance calculations. In all the mentioned research studies, no method has been proposed for online impedance calculation. In the following section, the suitable model for the network that surrounds the transmission line (was called external network) is introduced, and based on this model, the impedance relationships observed by the distance relay are formulated.

External network modeling

In this study, an appropriate model for the external network is presented, similar to the model proposed in (Eisa & Ramar, 2010; Izykowski et al., 2004; Wiszniewski, 1983). Then, using online information prior to fault occurrence and data stored in the relay memory, the parameters of this model are estimated. Ultimately, with the help of this model, fault location and fault resistance are accurately estimated upon occurrence of a fault.

Network Model Under Normal Operating Conditions

The models used for the external network in (Cook, 1986; Eriksson et al., 1985; Izykowski et al., 2004; Johns & Jamali, 1990; Novosel et al., 1996; Paladhi & Pradhan, 2017; Schweitzer III, 1983; Takagi et al., 1982) are not comprehensive, and their accuracy is sufficient only for networks where the communication path between transmission line terminals is the line itself (such as interregional or exchange lines). However, when a new communication path between transmission line terminals is added, their accuracy decreases. Given the vast and interconnected nature of today’s transmission networks, these models are inadequate for responding to various network configurations. Additionally, although a comprehensive network model is considered in (Eisa & Ramar, 2010; Izykowski et al., 2004; Wiszniewski, 1983), the main weakness of the algorithms proposed in these studies lies in their lack of online adaptability to different network configurations and their sensitivity to fault resistance values. The subsequent section describes the process of extracting an appropriate equivalent circuit for the external network.

Consider a fault-free transmission line in the network, denoted as line AB in Figure 1. In this network, each of the subsystems 1 to n represents a portion of the overall power system.

To model the transmission line shown in Figure 1, we cannot directly use the models employed in previous studies such as (Cook, 1986; Eriksson et al., 1985; Johns & Jamali, 1990; Novosel et al., 1996; Paladhi & Pradhan, 2017; Schweitzer III, 1983; Takagi et al., 1982). These models disregard the impedance of other communication paths between the terminals of line AB through the external network (depicted as ZAB in Figure 2). In this research, the external network is modeled using three impedances ZA, ZB, and ZAB, in conjunction with voltage sources EA and EB, as shown in Figure 2. Line AB with length L and impedance per unit length zl is represented by ZL.

Figure 1: The AB transmission line and the network that surrounds it

Figure 2: The external network equivalent circuit connected to line AB terminals

the network model under fault conditions in line AB.

The network state in Figure 2 prior to the fault occurrence, as depicted in Figure 3, involves current IAB=-IBA flowing from terminal A to terminal B through the external network. Additionally, injected currents ILA and ILB originate from terminals A and B, respectively, into line AB. Furthermore, IA and IB represent the injected currents from the external network to terminals A and B. The voltages at terminals VA and VB are also considered. In this context, F denotes the fault location, and d represents the distance from the fault location to terminal A (commonly known as the fault location).

In the modeling of single-phase-to-ground faults, as shown in Figure 4, the fault point is connected to the ground through a resistance Rf. The value of Rf can vary from zero to very high values. The presence of this resistance, when there is an injected current from the other terminal of the transmission line, leads to errors in fault resistance calculation and fault location estimation by the distance relay (Eriksson et al., 1985; Takagi et al., 1982).

Figure 3: Occurrence of single-phase to ground short-circuit fault in line AB

If we assume that the distance relay R is located at terminal A, the impedance seen by it can be calculated according to equation ‎(1). As shown in Figure 4, in this equation, the superscript f denotes the network quantities under fault conditions, VAf represents the voltage at terminal A, ILAf is the injected current from terminal A into line AB during the fault, ZR is the impedance seen by the distance relay and the unknowns Rf, If, and d correspond to the fault resistance, fault current, and fault location, respectively.

Since equation ‎(1) can be separated into real and imaginary parts, ultimately, we obtain a system of two equations with three unknown parameters. However, due to the greater number of unknown parameters than equations, a unique solution cannot be determined for this relationship.

|  | ZR=VAfILAf=d ZL+Rf IfILAf |
| --- | --- |

In (Takagi et al., 1982) proposed a solution for equation ‎(1) by separating the faulty network into two components: a fault free  network (pre fault conditions) and a pure fault network, as shown in Figure 5. They calculated the fault current based on the quantities related to the pure fault network. In this modeling approach, the network quantities in the faulted network are equal to the sum of corresponding quantities in the pre fault network and the pure fault network. Additionally, considering the difference in the magnitude of fault current and load current, it was assumed that the load remains constant during the fault occurrence, allowing the use of pre fault network data for the fault free network. The pure fault network quantities are calculated according to equations ‎(2), based on the corresponding quantities from the faulted network and the pre fault network. In these equations, the superscript f represents fault conditions, and the symbol ∆ denotes the quantities related to the pure fault network (without load current). For example, in equation ‎(2), the injected current from terminal A into line AB during the fault is denoted by ILAf, the corresponding quantity in the pre fault network (fault-free network) is ILA, and its contribution to the total fault current is represented by ∆ILAf. These quantities are illustrated in Figure 5.

Figure 4: Network model during fault occurrence in line AB

|  | ∆ILAf=ILAf-ILA ∆ILBf=ILBf-ILB ∆ILABf=ILABf-ILAB ∆If=If-0 ∆VLAf=VLAf-VLA ∆VLBf=VLBf-VLB |
| --- | --- |

The pure fault network is only excited by a current source of equivalent If, which makes the network act as a fault current divider. The contribution of injected fault current from each section to the total fault current If is shown by using the fault current distribution coefficient of that section (Eriksson et al., 1985). These coefficients are dimensionless. For instance, the coefficient for the current injected from terminal A to the fault location is denoted as kAf and is defined by equation ‎(3). It is calculated based on the impedances of the equivalent circuit, the impedance of line AB, and the fault location (Eriksson et al., 1985).

Figure 5: Separation of the faulted network into the pre fault network and the pure fault network

|  | kAf=∆ILAfIf =ZABZB+ZL+ZLZA+ZB-d(ZABZL+ ZLZA+ZB)ZABZA+ZB+ZL+ZLZA+ZB |
| --- | --- |

The term kAf can be written as equation ‎(4).

|  | kAf=K d+LM |
| --- | --- |

In this equation, the parameters M, K, and L are related to the impedance of the equivalent circuit and ZL. These parameters are independent of the fault location and can be calculated based on the relationships given in Equations (5)-(a), (b), and (c) (Saha et al., 2010).

|  | K=-(ZABZL+ ZLZA+ZB) (a) L=ZABZB+ZL+ZLZA+ZB (b) M=ZABZA+ZB+ZL+ZLZA+ZB (c) |
| --- | --- |

In three-phase networks, where the faults are generally asymmetrical, these coefficients for positive, negative and zero sequence networks are respectively represented by kA1f, kA2f, and kA0f, and are defined by relations ‎(6) (Saha et al., 2010).

The coefficients K1, L1, and M1 are calculated based on the impedances of the positive-sequence networks, while the coefficients K0, L0, and M0 are based on the impedances of the zero-sequence networks. The relationships for these coefficients are similar to those in Equations (5)-(a), (b), and (c). An important innovation in this research lies in estimating these coefficients using network structural information and online measurements.

|  | kA1f=ILA1fIF1=K1 d+L1M1 (a) kA2f=∆ILA2fIF2=kA2f (b) kA0f=ILA0fIF0=K0 d+L0M0 (c) |
| --- | --- |

For the network depicted in Figure 4, the fault current is expressed as a weighted sum of the sequence components of the fault current, as outlined in equation ‎(7). The coefficients a1f, a2f, and a0f are chosen based on the fault type, the phase in which the fault occurs, and various computational and technical considerations (Eriksson et al., 1985).

|  | If= a1f If1+a2f If2+a0f If0 |
| --- | --- |

By selecting weight coefficients in such a way that the zero-sequence component is eliminated, the fault current can be calculated according to equation ‎(8) (Eriksson et al., 1985).

|  | If=a1f ∆ILA1f+a2f ILA2f |
| --- | --- |

By utilizing equation ‎(6)-(a) and incorporating equation ‎(8) into equation ‎(1), one can derive the following expression ‎(9) to calculate the impedance observed by the distance relay:

|  | ZR=d ZL+Rf M1(a1f ∆ILA1f+a2f ILA2f)K1 d+L1 ILAf |
| --- | --- |

If we rewrite equation (9) in terms of d, we obtain equation (10) (Saha et al., 2010).

|  | K1ZL1d2+L1ZL1-K1ZR d-L1ZR +RfM1(a1f ∆ILA1f+a2f ILA2f)ILAf=0 |
| --- | --- |

If the coefficients K1, L1, and M1 are known in relation ‎(10), and considering that other parameters are known, then by separating this relation into its real and imaginary parts, the values of d and Rf can be accurately determined (Saha et al., 2010). To calculate the coefficients K1, L1, and M1, it is necessary to first determine the impedances ZA, ZB, and ZAB, which represent the configuration of the network shown in Figure 2.

Calculation of equivalent circuit parameters

If the thevenin impedances of the network in Figure 2 are named ZthA from the point of view of the terminal A and ZthB from the point of view of the terminal B, these impedances will be calculated according to the parameters of this network as described in the relations (11) and (12). In which the symbol ∥ is used to show that the impedances are parallel.

|  | ZthA=ZL∥ZAB+ZB∥ZA =ZAZLZAB+ZAZB(ZL+ZAB)ZLZAB+ZB(ZL+ZAB)+ZA(ZL+ZAB) |
| --- | --- |
|  | ZthB=ZL∥ZAB+ZA∥ZB= =ZBZLZAB+ZAZB(ZL+ZAB)ZLZAB+ZB(ZL+ZAB)+ZA(ZL+ZAB) |

If line AB is removed from the circuit in Figure 2, and thevenin impedances are recalculated from the viewpoint of terminals A and B, these impedances are respectively denoted as ZthA'  and ZthB', and are derived using relations ‎(13) and ‎(14).

|  | ZthA'=ZAB+ZB∥ZA=ZA(ZB+ZAB)ZA+ZB+ZAB) |
| --- | --- |
|  | ZthB'=(ZAB+ZA)∥ZB=ZB(ZA+ZAB)ZA+ZB+ZAB |

If the left sides of equations ‎(11), ‎(12), ‎(13), and ‎(14) are known, selecting any three of these equations and solving the resulting system (analogous to equation ‎(15)) will yield the unknown impedances of the network ZA, ZB, and ZAB.

|  | ZthA=ZAZLZAB+ZAZB(ZL+ZAB)ZLZAB+ZB(ZL+ZAB)+ZA(ZL+ZAB) ZthB=ZBZLZAB+ZAZB(ZL+ZAB)ZLZAB+ZB(ZL+ZAB)+ZA(ZL+ZAB) ZthA'=ZA(ZB+ZAB)ZA+ZB+ZAB) |
| --- | --- |

There are two methods for calculating the left side of the above equations (ZthA, ZthB, ZthA', and ZthB'). The first method is based on offline calculations and knowing the impedance of all network components. The second method is based on online measurement of the thevenin impedance of the network from the viewpoint of line terminals.

Offline Calculation of Equivalent Circuit Impedances

When the impedance data for all network components are available, it is possible to construct the network impedance matrix, known as Zbus. then, the network's thevenin impedances can be determined at the terminals of line AB. Specifically, if bus A aligns with row i and bus B with row j in the Zbus matrix, then the elements Zii and Zjj correspond to ZthA and ZthB, respectively. Moreover, if the Zbus matrix is configured in the line AB exit mode, the elements Zii and Zjj will correspond to ZthA' and ZthB', respectively. This method can be done for any network arrangement (including outages of lines, generators, transformers, and loads) to calculate the unknown impedances of the external network ZA, ZB, and ZAB for that arrangement.

Online Estimation of Equivalent Circuit Impedances

For the online estimation of the proposed equivalent circuit impedances, it is essential to initially identify the left side of relations ‎(11), ‎(12), ‎(13), and ‎(14), which represent the thevenin impedances of the network as seen from bus A and bus B. There are various methods for online estimation of thevenin impedances from the bus viewpoint (Abdelkader & Morrow, 2012; Arancibia et al., 2020; Yuan & Li, 2014). In this study, the technique introduced in (Abdelkader & Morrow, 2012) is used for estimating the online thevenin impedances of the network. For this purpose, load LA and LB have been selected for buses A and B, respectively. By following the voltage and current of these loads, the thevenin impedance of the network is calculated from the viewpoint of buses A and B.

Given that simultaneous access to the remote ends data of a transmission line is often possible at the relay installation terminal via a high-speed communication system, it is feasible to calculate the Thevenin impedancesZthA and ZthB at both terminals A and B and transmit them to the opposite terminal. However, calculating ZthA' and ZthB' under normal operating conditions is impractical, as disconnecting the transmission line during regular operation is not an option. Hence, an alternative practical solution must be considered.

Proposed Method for Online Estimation of Equivalent Circuit Impedances

The method proposed in this study to estimate the equivalent circuit impedances merges offline and online approaches. In summary, it encompasses the following steps:

Step 1 - Offline Database Formation:

By creating an offline database for relays using the method described in section ‎3-2-, the thevenin impedances ZthA, ZthB, ZthA', and ZthB' along with their corresponding equivalent impedances ZA, ZB, and ZAB are uniquely defined for various network configurations (Considering a single output for all network elements). The proposed offline impedance calculation algorithm, depicted in Figure 6, is implemented only upon the addition of a new device to the network. Subsequently, its results are updated offline in the relay's memory.

Step 2 - Online Calculation of thevenin Impedances from bus Viewpoint:

In this step, the impedances ZthA and ZthB are calculated online by monitoring the voltage and current of the loads at buses A and B. These calculated impedances are designated as ZthAonline and ZthBonline, and are recorded and preserved in the relay's memory. This process is carried out persistently and online throughout the operation of the relay.

Step 3 - Network Configuration Extraction (“new” Configuration):

In this step, using the online measurements made in step 2 (ZthAonline and ZthBonline)  and the offline information stored in the relay memory in step 1, the arrangement that ZthA and ZthB in it, has the smallest distance with ZthAonline and ZthBonline and satisfies the equation ‎(16), it is extracted from the relay memory. The extracted arrangement is named 'new' arrangement and the last previously selected arrangement is called 'old' arrangement. In equation ‎(16), i is the arrangement counter, Zi contains representative impedances of the ith arrangement, and ZTable contains all the arrangements stored in the relay memory.

|  | minZthAonline-ZthAi2+ZthBonline-ZthBi2 ∀Zi , Zi∈ZTable , |
| --- | --- |
|  | Zi=(ZthAi , ZthBi , ZthA'i , ZthB'i , ZAi , ZBi , ZABi) |

Step 4 - Selection of Final Network Configuration ('New' or 'Old' Configuration):

If the 'new' and 'old' configurations are the same, no specific action is needed, and the network configuration 'old' remains unchanged. However, if the 'new' configuration differs from the 'old' configuration, in order to mitigate the impact of system transient oscillations, the 'new' configuration must repeat at least K times within the last M 'new' configurations to be selected as the final network configuration. In this study, K=10 and M=20 are considered.

Figure 6: Proposed Offline Algorithm for Relay Database Formation

Figure 7: Proposed Adaptive Algorithm Flowchart

Step 5 - Correction of Potential Errors in Selecting the Correct Network Configuration:

If only line AB is disconnected from the network following a fault, while the other equipment connected to buses A and B remains energized (backup protection not operated, etc.), then using the information from the line terminals after the fault has cleared, ZthA' online and ZthB' online can be directly calculated. Then, upon solving the set of equations in equation ‎(15), the impedances of the equivalent circuit are determined. If the network configuration was not accurately identified in step 3, this step will ascertain the correct configuration at the time the fault occurred. Owing to the time-intensive aspect of this step, its data will serve to verify or rectify any potential mistakes in the network configuration determined in step 3 and to pinpoint the fault location again.

The five steps of the proposed method for online estimation of equivalent circuit impedances are delineated in the algorithm of Figure 7.

Proposed Adaptive Algorithm for Distance Relay

The adaptive algorithm proposed is designed to enhance the performance of the first and second zones of the distance relay at terminal A (denoted as RA) during a single-phase-to-ground fault on the transmission line AB. The input information for the algorithm, as depicted in the flowchart in Figure 7, is categorized into three main types:

Offline information:

Offline information encompasses the impedance values and configurations of network components, which are utilized to construct a relay database.

Remote online information:

Remote online information comprises the status of terminal B circuit breakers and the calculated Thevenin impedance at terminal B, determined by monitoring the voltage and current of load LB, and is employed to estimate the equivalent circuit impedances.

Local Online Information:

Local online information includes the status of terminal A circuit breakers, the voltage and current of load LA, and the current injected from terminal A to line AB. These parameters are utilized to determine the line’s status after the protection system operates, estimate the Thevenin equivalent impedance at terminal A, and perform distance relay calculations.

Using the input information above, the relay calculates the positive, negative, and zero sequence voltage and current quantities at terminal A. Subsequently, it calculates the impedance ZR, seen from terminal A, and in the event of a fault the following steps are executed:

Step 1-Instantaneous First Zone Trip:

For the first zone, an instantaneous trip is sent to the circuit breakers if the impedance ZR is less than the relay’s first zone setting.

Step 2 - Proposed Improvement of the First Zone:

In this step, for the voltage and current values of line AB, the last pre-fault values (stored in the relay memory) are considered as the fault-free network quantities ILA and VLA), and the received online values are considered as the faulted network quantities ILAf and VLAf. Then, using equations (2), the voltage and current values for the pure faulted network ∆ILAf and ∆VLAf are calculated. Now, using the estimated equivalent impedances of the network (output of Step 4 in Section ‎3-4-) and solving the equation ‎(10), the fault location and fault resistance (d and Rf) are calculated. If the fault location falls within 80% of the length of line AB, an instantaneous trip command is sent to the circuit breakers.

Step 3 - Proposed Improvement of the Second Zone:

In this step, if the fault location is within the last 20% of the length of the line AB or ZR is less than the relay second zone setting, a delayed trip command with T1 time delay is sent to the circuit breakers.

Step 4 - Third Zone Operation:

If ZR is less than the relay third zone setting, a delayed trip command with T2 time delay is sent to the circuit breakers.

Implementation of the Proposed Method

To validate the proposed method, this algorithm has been implemented on the IEEE 39-bus standard network (Zimmerman & Murillo-Sánchez, 2016). For the purposes of this study, the existing transmission line between bus 4 and bus 14 was selected, and for calculating the thevenin impedance of the network from a view point of bus 14, a load in bus 14 (L14) with a power of 100+j153 MVA at bus 14 was considered. The arrangement of the 39-bus network with the addition of load L14 is shown in Figure 8.

Figure 8: IEEE 39-Bus Standard Network with the Addition of Load L14

To investigate the performance of the proposed adaptive algorithm, this algorithm is implemented on relay R4 (which is installed at terminal 4 of line 4-14 according to Figure 8, and their performance, before and after applying the proposed algorithm, is compared. Relay R4 is a Siemens 7SA522 model with polygonal regions Z1, Z2, and Z3 activated in the forward direction. The settings of this relay are based on (Ziegler, 2011) and are done as shown in Table 1, and its characteristic with these settings is shown in Figure 9.

Table 1: The R4 Relay Settings

| Zone | Z1 |  | Z2 |  | Z3 |  |
| --- | --- | --- | --- | --- | --- | --- |
| Z (ohm) | R1 | X1 | R2 | X2 | R3 | X3 |
| primary | 25.00 | 12.28 | 34.99 | 19.98 | 42.09 | 36.01 |
| Secondary | 7.97 | 3.92 | 11.16 | 6.37 | 13.71 | 11.48 |

Figure 9: The R4 relay characteristic

Preparation of R4 relay database

By forming the Zbus matrix for the base state (the state of all network elements being in circuit) of the network shown in Figure 8, the thevenin impedances from the viewpoint of the line 4-14 terminals are determined. These impedances are calculated for two scenarios: when line 4-14 is in the circuit (Zth4 and Zth14) and when it is out of the circuit (Zth4'  and  Zth14'), as detailed in Table 2. As mentioned, these impedances are the left-hand side values of relations ‎(11), ‎(12), ‎(13), and ‎(14), for the base state of the Figure 8 network.

Table 2: Network thevenin Impedances from the viewpoint of line 4-14 terminals

| Zth4(Ω) | Zth14(Ω) | Zth4'(Ω) | Zth14'(Ω) |
| --- | --- | --- | --- |
| 2.40+29.48i | 2.56+31.21i | 2.69+33.07i | 3.24+38.33i |

By solving the system of equations in relation (15), the impedances of the equivalent circuit proposed in Figure 2 are calculated as described in Table 3. These impedances represent the base arrangement of the network shown in Figure 8, and the removal of any element from this network will result in a variation of these impedances.

Table 3: Equivalent circuit impedances of the base arrangement of Figure 8 network

| ZA(Ω) | ZB(Ω) | ZAB (Ω) |
| --- | --- | --- |
| 3.78+47.39i | 5.83+66.67i | 3.49+42.80i |

The methodology for creating Table 2 and Table 3, encompassing all network configuration possibilities by adhering to the N-1 criterion (considering single equipment outages), follows the procedure outlined in Figure 6 to finalize the relay R4 database.

Case Study-1

In the first case study, it is assumed that all elements of the network in Figure 8 are energized. According to the scenarios introduced in each row of Table 4, each time a single-phase ground fault occurs along line 4-14, the performance of relay R4 is examined before and after applying the proposed algorithm to it. In Table 4, the parameters Rfac and dac are the actual resistance and location (relative to the origin of bus 4) of the fault, respectively, Zac refers to the accurate and actual zone where faults occur, and Ds refer to defined scenarios.

Table 4: Defined scenarios for case study-1

| Zac | dac(%) | RfacΩ | Ds |
| --- | --- | --- | --- |
| Z1 | 20 | 0 | S1 |
| Z1 | 50 | 0 | S2 |
| Z1 border | 80 | 0 | S3 |
| Z1 | 20 | 0.5 | S4 |
| Z1 | 50 | 0.5 | S5 |
| Z1 border | 80 | 0.5 | S6 |
| Z1 | 20 | 5 | S7 |
| Z1 | 50 | 5 | S8 |
| Z1 border | 80 | 5 | S9 |
| Z1 | 20 | 20 | S10 |
| Z1 | 50 | 20 | S11 |
| Z1 border | 80 | 20 | S12 |

With the application of defined faults in scenarios S1 to S12 on line 4-14, the performance of relay R4 before applying the proposed algorithm is as described in Table 5. As observed, with the increase in fault resistance and the fault location moving away from bus 4, relay R4 makes mistakes and cannot detect the fault in the correct protective zone. In the case of scenario S12, the situation is more severe because due to the high fault resistance and the remote location of the fault, despite the presence of a fault along line 4-14 (zone Z2), it has no performance. In Table 5, the parameters Rfcal and dcal are respectively the resistance and location (relative to the origin of bus 4) of the fault calculated by the relay, RR and XR are respectively the real and imaginary parts of the impedance seen by relay R4, Opz indicates the protection zone that has been operated, and Fct denotes the sum of the circuit breaker's operational time and the relay's time delay for the operated zone, known as the fault clearing time, measured per second.

Table 5: Output of Relay R4 for case study-1 scenarios before applying the proposed algorithm to it

| dcal% | RfcalΩ | Opz | Fct (s) | XR Ω | RR Ω | Ds |
| --- | --- | --- | --- | --- | --- | --- |
| 19.99 | 0.00 | Z1 | 0.02 | 3.07 | 0.19 | S1 |
| 50.02 | 0.00 | Z1 | 0.02 | 7.68 | 0.48 | S2 |
| 79.98 | 0.00 | Z1 | 0.02 | 12.28 | 0.76 | S3 |
| 21.03 | 0.83 | Z1 | 0.02 | 3.07 | 1.02 | S4 |
| 50.82 | 0.98 | Z1 | 0.02 | 7.68 | 1.46 | S5 |
| 80.93 | 1.23 | Z2 | 0.32 | 12.29 | 1.99 | S6 |
| 58.40 | 8.25 | Z1 | 0.02 | 3.08 | 8.44 | S7 |
| 83.89 | 9.87 | Z2 | 0.32 | 7.71 | 10.35 | S8 |
| 116.88 | 12.29 | Z2 | 0.32 | 12.37 | 13.05 | S9 |
| 210.34 | 32.02 | Z3 | 0.62 | 3.1 | 32.21 | S10 |
| 264.80 | 39.50 | Z3 | 0.62 | 7.81 | 39.98 | S11 |
| 344.66 | 50.74 | out of zone | - | 12.61 | 51.5 | S12 |

By applying the proposed algorithm to relay R4, the results obtained for the 12-fold scenarios are as described in Table 6. It is worth mentioning that for the 12-fold scenarios, the same values of Table 2 for the thevenin impedances of the network from the viewpoint of the terminals of line 4-14 are obtained, and this issue was confirmed by running the proposed algorithm for these scenarios.

Table 6: Output of Relay R4 for case study-1 scenarios after applying the proposed algorithm to it

| dcal% | RfcalΩ | Opz | Fct (s) | XR Ω | RR Ω | Ds |
| --- | --- | --- | --- | --- | --- | --- |
| 20 | 0.00 | Z1 | 0.02 | 3.07 | 0.19 | S1 |
| 50.01 | 0.00 | Z1 | 0.02 | 7.68 | 0.48 | S2 |
| 80.00 | 0.00 | Z1 | 0.32 | 12.28 | 0.76 | S3 |
| 20.01 | 0.50 | Z1 | 0.02 | 3.07 | 1.02 | S4 |
| 50.09 | 0.51 | Z1 | 0.02 | 7.68 | 1.46 | S5 |
| 80.08 | 0.51 | Z2 | 0.32 | 12.29 | 1.99 | S6 |
| 20.95 | 5.02 | Z1 | 0.02 | 3.08 | 8.44 | S7 |
| 51.14 | 5.04 | Z1 | 0.02 | 7.71 | 10.35 | S8 |
| 81.26 | 5.07 | Z2 | 0.32 | 12.37 | 13.05 | S9 |
| 21.54 | 20.01 | Z1 | 0.02 | 3.1 | 32.21 | S10 |
| 51.54 | 20.8 | Z1 | 0.02 | 7.81 | 39.98 | S11 |
| 81.09 | 20.74 | Z2 | 0.32 | 12.61 | 51.5 | S12 |

As can be seen in Table 6, in addition to all faults being detected in the relevant protective zone, the resistance and location of the fault occurrence have also been calculated with very high accuracy by the relay.

Case Study-2

In the second case study, it is assumed that line 18-17 has been disconnected from the circuit before a fault occurs on line 4-14, and the network has reached steady state. Under these new conditions, the scenarios of case study-1, before and after applying the proposed algorithm, are examined. By applying the defined scenarios S1 to S12 on line 4-14, the performance of relay R4 before applying the proposed algorithm is as described in Table 7.

Table 7: Output of Relay R4 for case study-2 scenarios before applying the proposed algorithm to it

| dcal% | RfcalΩ | Opz | Fct (s) | XR Ω | RR Ω | Ds |
| --- | --- | --- | --- | --- | --- | --- |
| 19.99 | 0.00 | Z1 | 0.02 | 0.19 | 3.07 | S1 |
| 50.02 | 0.00 | Z1 | 0.02 | 0.48 | 7.68 | S2 |
| 79.98 | 0.00 | Z1 | 0.02 | 0.76 | 12.28 | S3 |
| 21.16 | 0.89 | Z1 | 0.02 | 1.08 | 3.07 | S4 |
| 50.90 | 1.05 | Z1 | 0.02 | 1.53 | 7.68 | S5 |
| 81.03 | 1.32 | Z2 | 0.32 | 2.08 | 12.29 | S6 |
| 62.12 | 8.87 | Z1 | 0.02 | 9.06 | 3.04 | S7 |
| 87.45 | 10.58 | Z1 | 0.02 | 11.06 | 7.66 | S8 |
| 120.65 | 13.14 | Z2 | 0.32 | 13.90 | 12.30 | S9 |
| 232.52 | 35.46 | Z3 | 0.62 | 35.65 | 2.93 | S10 |
| 282.76 | 42.35 | out of zone | - | 42.83 | 7.60 | S11 |
| 355.82 | 52.57 | out of zone | - | 53.33 | 12.34 | S12 |

As can be seen, with the increase in fault resistance and the fault location moving away from bus 4, due to the increased effect of the injected current from the remote terminal of the transmission line to the fault location, relay R4 makes mistakes and cannot detect the fault in the correct protective zone. This issue is shown in scenarios S11 and S12, where despite the presence of a fault along line 4-14 (border of zones Z1 and Z2), the relay does not see the fault and has no performance. The analysis and review of the data in Table 5 and 7 emphasize the vital role of adaptive settings of relay R4 in correctly detecting high-resistance faults and demonstrate the importance of having adaptive relay settings in accordance with network structural changes.

By applying the proposed algorithm to relay R4, the defined 12-fold scenarios in Table 4 are again executed on line 4-14. Table 8 contains the output results of relay R4 for each of these scenarios.

Table 8: The output of relay R4 for case study-2 scenarios after applying the proposed algorithm to it

| dcal% | RfcalΩ | Opz | Fct (s) | XR Ω | RR Ω | Ds |
| --- | --- | --- | --- | --- | --- | --- |
| 20 | 0.00 | Z1 | 0.02 | 3.07 | 0.19 | S1 |
| 50.01 | 0.00 | Z1 | 0.02 | 7.68 | 0.48 | S2 |
| 80.01 | 0.00 | Z2 | 0.32 | 13.82 | 0.86 | S3 |
| 20.01 | 0.50 | Z1 | 0.02 | 3.07 | 1.00 | S4 |
| 50.09 | 0.51 | Z1 | 0.02 | 7.68 | 1.44 | S5 |
| 80.35 | 0.51 | Z2 | 0.32 | 13.83 | 2.16 | S6 |
| 20.95 | 5.02 | Z1 | 0.02 | 3.08 | 8.28 | S7 |
| 51.14 | 5.04 | Z1 | 0.02 | 7.72 | 10.14 | S8 |
| 81.29 | 5.07 | Z2 | 0.32 | 13.94 | 13.94 | S9 |
| 21.54 | 20.01 | Z1 | 0.02 | 3.13 | 32.53 | S10 |
| 51.54 | 20.8 | Z1 | 0.02 | 7.83 | 39.15 | S11 |
| 80.89 | 21.04 | Z2 | 0.32 | 14.29 | 53.17 | S12 |

The outage of line 17-18 alters the Thevenin impedances from the view point of line 4-14 terminals. These impedances are computed online as the proposed algorithm runs and remain consistent across all 12-fold scenarios, owing to the network's fixed configuration. The values for this case study can be found in Table 9.

Table 9: The thevenin impedances from the viewpoint of the line 4-14 terminals in the case of line 17-18 outage.

| Zth4(Ω) | Zth14(Ω) | Zth4'(Ω) | Zth14'(Ω) |
| --- | --- | --- | --- |
| 2.46+30.02i | 2.56+31.22i | 2. 91+34.87i | 3.32+38.84i |

By solving the system of equations in relation (15), the impedances of the proposed equivalent circuit in Figure 2 are calculated as described in Table 10. These impedances correspond to the Figure 8 network arrangement in the case of line 17-18 outage.

Table 10: The equivalent circuit impedances for the Figure 8 network arrangement in the case of line 17-18 outage.

| ZA(Ω) | ZB(Ω) | ZAB (Ω) |
| --- | --- | --- |
| 4.10+50.19i | 5.34+62.88i | 4.66+51.40i |

Conclusion

Protection systems play a crucial role in power system performance. Their fast and accurate performance is essential for optimal power system operation. When faults occur, minimizing damage to equipment and the network becomes critical. Additionally, quickly identifying fault locations reduces recovery time for the post-faulted network. In power transmission networks, these requirements are even more pronounced due to the network’s size and the substantial energy transmitted. To address these challenges, a novel adaptive algorithm for distance relays in interconnected power networks has been proposed. This algorithm improves relay performance in both the first and second protection zones (Z1 and Z2) while accurately calculating fault locations. Furthermore, it is robust against changes in network arrangement and can effectively detect high-resistance faults. Simulation results and case studies demonstrate that applying this algorithm enhances relay performance compared to conventional distance algorithms. By reducing network recovery time and maintaining system reliability, this adaptive algorithm contributes to a more efficient power system operation.

References

Abdelkader, S. M., & Morrow, D. J. (2012). Online tracking of Thévenin equivalent parameters using PMU measurements. IEEE Transactions on Power Systems, 27(2), 975-983.

Anderson, P. M., Henville, C. F., Rifaat, R., Johnson, B., & Meliopoulos, S. (2022). Power system protection. John Wiley & Sons.

Arancibia, A., Soriano–Rangel, C. A., Mancilla–David, F., Ortega, R., & Strunz, K. (2020). Finite–time identification of the Thévenin equivalent parameters in power grids. International Journal of Electrical Power & Energy Systems, 116, 105534.

Cook, V. (1986). Fundamental aspects of fault location algorithms used in distance protection. IEE Proceedings C (Generation, Transmission and Distribution),

Eisa, A. A. A., & Ramar, K. (2010). Accurate one-end fault location for overhead transmission lines in interconnected power systems. International Journal of Electrical Power & Energy Systems, 32(5), 383-389. https://doi.org/10.1016/j.ijepes.2009.11.005

Eriksson, L., Saha, M. M., & Rockefeller, G. (1985). An accurate fault locator with compensation for apparent reactance in the fault resistance resulting from remore-end infeed. IEEE Transactions on Power apparatus and systems(2), 423-436.

Horowitz, S. H., Phadke, A. G., & Henville, C. F. (2022). Power system relaying. John Wiley & Sons.

Igberaese, S. E., Tsado, J., & Gana, J. (2023). The Conventional Distance Protection scheme for 132 kV Transmission lines–A.

Izykowski, J., Rosolowski, E., & Saha, M. M. (2004). Locating faults in parallel transmission lines under availability of complete measurements at one end. IEE Proceedings-Generation, Transmission and Distribution, 151(2), 268-273.

Johns, A., & Jamali, S. (1990). Accurate fault location technique for power transmission lines. IEE Proceedings C (Generation, Transmission and Distribution),

Nikolaidis, V. C., Tsimtsios, A. M., & Safigianni, A. S. (2018). Investigating particularities of infeed and fault resistance effect on distance relays protecting radial distribution feeders with DG. IEEE Access, 6, 11301-11312.

Novosel, D., Hart, D. G., Udren, E., & Garitty, J. (1996). Unsynchronized two-terminal fault location estimation. IEEE Transactions on Power Delivery, 11(1), 130-138.

Paladhi, S., & Pradhan, A. K. (2017). Adaptive zone-1 setting following structural and operational changes in power system. IEEE Transactions on Power Delivery, 33(2), 560-569.

Panahi, H., Zamani, R., Sanaye-Pasand, M., & Mehrjerdi, H. (2021). Advances in transmission network fault location in modern power systems: Review, outlook and future works. IEEE Access, 9, 158599-158615.

Saha, M. M., Izykowski, J., & Rosolowski, E. (2010). Fault location on power networks (Vol. 2). Springer.

Sarangi, S., Sahu, B. K., & Rout, P. K. (2021). Review of distributed generator integrated AC microgrid protection: issues, strategies, and future trends. International Journal of Energy Research, 45(10), 14117-14144.

Schweitzer III, E. O. (1983). Evaluation and development of transmission line fault-locating techniques which use sinusoidal steady-state information. Computers & electrical engineering, 10(4), 269-278.

Takagi, T., Yamakoshi, Y., Yamaura, M., Kondow, R., & Matsushima, T. (1982). Development of a new type fault locator using the one-terminal voltage and current data. IEEE Transactions on Power apparatus and systems(8), 2892-2898.

Wiszniewski, A. (1983). Accurate fault impedance locating algorithm. IEE Proceedings C (Generation, Transmission and Distribution),

Yuan, H., & Li, F. (2014). A comparative study of measurement-based thevenin equivalents identification methods. 2014 North American Power Symposium (NAPS),

Ziegler, G. (2011). Numerical distance protection: principles and applications. John Wiley & Sons.

Zimmerman, R. D., & Murillo-Sánchez, C. E. (2016). Matpower 6.0 user’s manual. Power Systems Engineering Research Center, 9.