A Physics-Driven Approach for Identifying Leakage Users in Low-Voltage Distribution Systems

Li Bin1, Feng Xiaofei1, Su Sheng1, Zhong Peijun1, Xiao Hao2

1 Changsha University of Science and Technology, Changsha, 410114 China

2 University of Manitoba, Winnipeg, MB, Canada

Corresponding author: Su Sheng (e-mail: eessheng@163.com).
“ This work was supported in part by the Natural Scientific Research Funding of China under Grant 51777015.”

ABSTRACT Wiring faults, caused by improper connections between neutral lines and protective earth (PE) lines due to negligence by electrical technicians, are a prevalent type of earth fault in low-voltage distribution systems (LVDS). These faults can cause the load current of affected users to flow back to the transformer's neutral point via the PE line as residual current, leading to nuisance tripping of residual current devices (RCDs). To maintain normal power supply, users may disable RCDs, which compromises safety and can result in severe hazards such as electric shocks and electrical fires. This paper proposes a method to locate users with wiring faults by leveraging abundant metering data within LVDS and utilizing leakage fault analysis devices. We construct a linear model of residual current considering multiple fault scenarios. Based on this model, a multiple linear regression (MLR) approach is developed to identify and locate anomalous users by analyzing the correlation between their load currents and the residual current of the LVDS. Experimental results under various scenarios validate the performance of the proposed method.

INDEX TERMS Low-voltage distribution system, Wiring fault users, Earth fault, Residual current devices

INTRODUCTION

- Wiring faults, characterized by improper connections between neutral lines and protective earth (PE) lines in user distribution boards, are a prevalent type of earth fault in low-voltage distribution systems (LVDS). Often resulting from negligence by electrical technicians, wiring faults cause the load current of the affected user to return via the PE line as residual current. This can result in severe consequences such as electric shocks and electrical fires, endangering both life and property.

- Previous research on earth faults in LVDS has primarily focused on insulation failures and associated arc leakage problems, such as insulation breaches in lines or equipment and unintended contact between live conductors and enclosures [1], [2]. Detection and protection against such faults are typically implemented using relay protection principles and RCDs in combination with grounding protection schemes [3]. Various methods—including support vector machines [5], fuzzy neural networks [6], and wavelet packet transforms [7]—have been employed to detect earth fault currents, extract salient current features, and ascertain fault types. These approaches have enhanced the protective efficacy of RCDs by enabling real-time monitoring and intelligent isolation of leakage sources [8-9].

- However, wiring faults differ significantly from insulation-related earth faults. They exhibit robust electrical connections without characteristic arc discharge features, impeding the effectiveness of intelligent algorithms designed for insulation failure detection [10]. Existing criteria for fault determination often rely on empirical knowledge, which is insufficient to cover the wide array of earth fault types encountered in practice, leading to maloperations and nuisance tripping of RCDs [11]. Moreover, when users are unable to pinpoint and rectify earth faults, RCDs stationed either on the low-voltage side of distribution transformers or on branch line distribution boards become prone to nuisance tripping. This results in recurrent power interruptions for the associated users [12-13], compelling them to disable the RCDs, which poses significant threats to user safety [14-15].

- Given the pervasive risks posed by wiring faults, there is an urgent need for reliable and effective methods to detect and locate such faults. The advent of smart grids and the integration of Internet of Things (IoT) technologies have provided new opportunities to address this challenge [16]. Smart meters equipped with IoT capabilities collect high-density metering data, including residual currents and user load currents, facilitating non-invasive analyses to uncover correlations between abnormal residual currents and the load currents of users with wiring faults [17]. This data richness enables the development of novel approaches for fault localization and troubleshooting in LVDS.

- In this paper, we propose a method to identify and locate users with wiring faults to prevent unnecessary RCD tripping. We construct a linear model of residual current within LVDS, considering scenarios with one or multiple users having wiring faults. Based on this model, we develop a multiple linear regression (MLR) approach to analyze the correlation between user load currents and the residual current of the LVDS.

- The principal contributions of this work are:

- Highlighting the Risks of Wiring Faults: We emphasize that wiring faults are a common type of earth fault in LVDS, causing RCD nuisance tripping and leading users to disable RCDs, which increases safety hazards such as electric shocks and fires.

- Analyzing Residual Current Characteristics: We analyze the characteristics of residual current data across different wiring fault scenarios—including single-user and multi-user wiring faults on the same or different phases—and explore the correlation between abnormal residual currents and the load currents of the implicated users.

- Proposing a Localization Method: We propose and validate a localization method employing MLR analysis for identifying users with wiring faults, leveraging high-density metering data from smart meters, thereby bridging a conspicuous research gap in this domain.

- The remainder of this paper is organized as follows: Section II examines the mechanism and impact of wiring faults. Section III describes the variation characteristics of residual currents in different scenarios. Section IV introduces the localization method based on the MLR model. Section V presents experimental results to validate the proposed method. Finally, Section VI concludes the paper.

MECHANISM AND INFLUENCE OF WIRING FAULTS

In the field, the reverse connection of neutral line and PE line caused by reckless users are very common behind the user panel box. Fig. 1 shows a LVDS with wiring fault users and leakage path.

As shown in Fig. 1, the yellow dashed box indicates the installation position of RCDs. The current I0, I1 and I2 represents the action threshold of the third RCD, second RCD, and first RCD, respectively. The load current of the user 2 flow back to the neutral point of the distribution transform through the earth rather than the neutral line, when the neutral line and the PE line of the user 2 are reversed. At this point, the live current of the secondary distribution board is composed of the load currents of user 1 and user 2, while the neutral current of the secondary distribution board only includes the neutral current of the user 1. That is, the load current of the wiring fault user 2 will be converted into the residual current of the LVDS. At this time, the residual current is mainly composed of the load current of the user 2, which increases sharply and fluctuates similarly with the

load current. If this wiring fault is persisting in the LVDS, the electricity behavior of the anomaly user 2 will cause RCD to trip frequently and intermittently. Since it is difficult to accurately locate and isolate the wiring fault, power utilities have to withdraw the installed RCD to ensure power supply, which induces a serious threat to the electricity safety of users.

A diagram of LVDS with wiring fault users.

The scheme of TT earthed is widely used in distributed households and rural users to supply power and ensure the electrical safety of users, in which the neutral point and the exposed conductive part of the electrical equipment are directly earthed instead of a separate protective earth line from the side of the distribution transformer, and the PE lines of several households are usually connected to a unified plate earthed on site. When the neutral line and the PE line are connected in reverse, the load current will flow into the PE line and it is possible to burn or break the terminal of the PE line, which will fail the protection of the PE line, charge the conductive enclosure of the household appliance connected to the PE line, and greatly increase the risk of users’ safety [18].

Although wiring faults are common in LVDS, if the RCD is withdrawn, the wiring fault will not affect users’ power consumption, which makes this earth fault always difficult to locate. Therefore, it is of great significance to make efforts on the detection and location method for the leakage in the LVDS caused by the reverse connection between the neutral line and PE line of users, for the safety of users.

Leakage fault analysis devices in LVDS.

RCDs only highlight speed of protection action and cannot be used for analysis of the residual current variation and location of earth faults due to the lack of data recording capability [19-21]. In recent years, meters have been equipped with HPLC module, which make it possible to report metering data with 15-minute interval or higher density.

As nodes within the LVDS, smart meters not only undertake high-density measurements of electrical variables at their respective location, including current, voltage, power and phase, but they also network with other smart meters and maintain close contact with the electricity information acquisition system. The relationship is depicted in Fig. 2.

Power maintenance staff can utilize the high-density electrical data collected by each smart meter to carry out a variety of in-depth applications. These applications include basic tasks such as topology identification and etc., which lay the foundation for more advanced applications. With the established basic information, the staff can further perform fault monitoring, outage reporting, abnormal electricity usage detection, and clock synchronization. These advanced applications expand the scope of services provided by power utilities. Moreover, they effectively enhance the proactive service capabilities of the maintenance staff [22]. We have developed a leakage fault analysis devices that provides strong support for the vigilant monitoring and detailed analysis of changes in residual current. The residual current is composed of components such as the UPS analog power supply, voltage converter, core, LCD, and a leakage current sensor. Due to cost considerations, the devices is typically installed on the low-voltage side of the distribution transformer, enabling comprehensive monitoring of residual current fluctuations across the entire LVDS.

Profiles of natural leakage current and load current.

RESIDUAL CURRENT ANALYSIS OF WIRING FAULTS

The following analysis aims to investigate the relationship between the residual current and each user's load current under different wiring fault scenarios, taking into account the differences in users' phases. When a wiring fault occurs in LVDS, the residual current includes load current of abnormal user, will fluctuate significantly as the user's electricity usage behavior changes. Through the data collection capabilities of IoT meters with HPLC, it becomes feasible to record in detail the fluctuations of residual current and each user's load current during the fault, thereby distinguishing between normal and abnormal users. However, the phase to which each user in the LVDS belongs may vary. Moreover, the composition of the residual current differs under various wiring fault scenarios. The analysis is further differentiated between wiring fault of single-user and multi-user, taking into account the differences in users' phases. Using the case of a two-user wiring fault as an example, the composition of the residual current is analyzed separately for same-phase two-user wiring fault and different-phase two-user wiring fault.

- Single-user with Wiring Fault

In the scenario of single-user with wiring fault, the residual current of LVDS and load current of users are recorded every 15 minutes throughout a day based on the smart meter. The fluctuation of residual current and load current is shown in Fig. 2, where horizontal axis denotes the time sequence of 96 metering points in a day, and longitudinal axis on the left and right denotes the scale of load current and residual current.

In Fig. 3, it can be seen that the natural leakage current in the LVDS fluctuates below 70 mA. Since the LVDS has a slight natural residual current during normal operation, it can be assumed that there is no obvious earth fault and the residual current in the LVDS of distribution transformer can be expressed as:

where  denotes residual current in the LVDS and  denotes natural leakage current of the LVDS.

The first RCD is designed to respond to the anomaly residual current of the entire the LVDS and isolate earth fault with a typical residual current threshold of 300mA. As shown in Fig.3, the natural leakage current of the LVDS always fluctuate below the threshold of RCD.

Profiles of the load current and anomaly residual current of the LVDS.

Different with the slight fluctuation of natural leakage current within a small scale, the load current of LV user will fluctuate greatly with the change of electricity usage. When the connection of neutral line and PE line of a user is reversed, the residual current of the LVDS is equal to the vector sum of the natural leakage current and the load current of the user with wiring fault, which can be expressed as

Where represent the load current of the user with the wiring fault. Since the load current of the user is usually several amperes or tens and much larger than the natural leakage current, the residual current of the LVDS would increase sharply and leads to RCD tripping, when the neutral line and PE line of a user is reversed.

- Multiple-user with Wiring Fault

In the LVDS, there may also exist a situation that the neutral line and the PE line of double users are reversed at the same time. Thus, it is necessary to analyze the wiring fault separately when the double users belong to the same or different phase, and then the residual current of the LVDS can be expressed by

where  represent load current of user m in phase x, and  represent load current of user n in phase y.

When there are two users with wiring fault in the LVDS, if both users operate in the same phase, it can be approximately considered that there is no phase angle difference between the load current of the two users, and the residual current of the LVDS is also equal to the arithmetic sum of the load current of the two users. When the two users operate in different phases, the phase angle difference of their load current is approximately 120°, and the residual current is equal to the vector sum of the load current of two users at that time. Fig. 4 illustrates the residual current curves of the LVDS in the two situations described above, along with the load current curves of the two users responsible for the abnormal magnitude change in the residual current.

As we can see, the residual current curve of the LVDS in both cases have drastic magnitude fluctuation for the electrical behavior of wiring fault users. However, there is still a clear similarity with the user load current in curve shapes such as peaks and valleys. The scenario of double users with wiring fault is more complex and it will bring greater challenges to the location of the leakage fault in the LVDS.

In summary, the leakage current of the LVDS have close relationship with the load current of anomaly user when there are wiring faults in the LVDS. Based on this characteristic, the anomaly user that cause excessive residual current can be accurately located, which will ensure the normal operation of the selective protection of the RCD and the electrical safety of users.

MLR based Earth Fault Location in LVDS

A. Multiple Linear Regression

In the LVDS, each user has the same potential of wiring fault and will cause excess residual current. In order to identify and locate anomaly user, it is necessary to quantitatively determine the contribution of load current of each user to the residual current in the LVDS. The MLR is a statistical method to estimate the relationship between multiple independent variables and dependent variables [23-25]. Since the residual current of the LVDS varies simultaneously with the load current of wiring fault user, its relevance can be analyzed by constructing MLR model based on the time sequence of the load current of users and the residual current in the LVDS and used it to identify anomaly users. The composition of residual current of the LVDS with N users can be expressed as

Where the dependent variable Y denotes the residual current flowing into the primary distribution board of the associated distribution transformer; the independent variable X1, X2, …, XN denote the load current of the associated users in the same LVDS; 1, 2, …, n denote regression coefficients; 0 denotes regression constant; and  denotes random error caused by objective factors. Regression coefficients can be estimated by solving the linear equations of the N equations. Therefore, T groups of observation data xi,1, xi,2, …, xi,n, yi (i=1, 2, …, T, T≥n) obtained from metering devices is used to establish linear equations. The linear regression model can be expressed as

The above Eq. (5) can be written as

Substituting T groups of metered data of load current and residual current into Eq. (6), the linear equations can be solved to calculate the estimated parameters of regression coefficients. Then the estimated linear regression model can be expressed as

Where  denotes the estimation of the observed value , j means at time j. Taking the result into a condition, and the SSE can be calculated by

Where SSE denotes the residual sum of squares between the sample value and the estimated value of Y. According to the least squares estimation,  are known as the least squares estimation of the regression coefficient 1, 2, …, n and constant 0, when the value of SSE is minimum. Based on calculus knowledge and extremum principle on multivariate function, just calculate the first-order partial derivative of the parameter to be estimated by SSE and make its value equal to zero, and the normal equations of the estimated parameters can be obtained by

The normal equations can also be expressed as

Once the inverse matrix of (XTX) is available, the least squares estimate of the regression coefficients can be calculated by

The value of these regression coefficients calculated above also map the influence degree of the independent variables on the dependent variables, that is, the impact of the load current of users on the residual current of the LVDS. The anomaly users will finally be located when the investigation of this model can be satisfied. Therefore, this MLR model established above should be finally examined with a series of statistical indicators to verify its reliability, as follows.

•Multiple correlation coefficient. This is an indicator which represents the degree of linear relationship between the independent and dependent variables. The multiple correlation coefficient R indicate the stronger linear relationship between the independent and dependent variables, when R is closer to 1.

• Determination coefficient. This indicator is expressed by R2, which can be used to weigh the fit of MLR models and can be calculated by

Where SST denotes the total sum of squares, SSR denotes the sum of squares caused by regression, and SSE denotes the sum of squared errors. The determination coefficient R2 ranges between 0 and 1, with a greater value indicating a better fit of the regression model. However, it should be noted that a system with more independent variables will have a larger determination coefficient R2. In addition to determining the fitting effect of the equation based on the determination coefficient, other test standards also should be adopted.

•F-test. This test method uses analysis of variance to test whether the regression model is reasonable at a certain significance level. If  in this model, it can be considered that the model passed the significant test of F-test. Where k denotes the number of independent variables in the regression model and N denotes the capacity of independent variables.

•T-test. It is also known as the test of partial regression coefficients and constant term. The T-test can be used to determine the significance level of the regression coefficient and the constant term on the regression model, as well as the sufficiency of the independent variables entering the equation.

B. Multicollinearity Problem

The current curves of some users are familiar to each other since their lifestyle and electricity consumption are similar, which indicates that there is a certain degree of multicollinearity between the time sequence of load current of each user. The similarity violates the classical assumption that there is no correlation between independent variables and leads to the unreliability of the MLR model. Therefore, it is necessary to conduct multicollinearity test for these independent variables before implementing MLR analysis.

When the dependent variable of MLR model can be organized as

If  are incompletely equal to zero, which means that these independent variables have multicollinearity trouble. While these independent variables of MLR model can be organized as

Where are incompletely equal to zero,  denotes a random disturbance term, and it is said that these independent variables  have approximate multicollinearity.

Even if the independent variable has a little multicollinearity, it can lead to an increase in the variance and covariance of the least squares estimate of the regression coefficients, which is meaningless for the entire regression model. Therefore, variance inflation factor (VIF) is introduced as an indicator which can characterize the severity of multicollinearity in MLR models [26]. Constructing an auxiliary regression model with Xj as the dependent variable i, the VIFj of Xj can be calculated by Eq. (15), when the independent variables are not linearly correlated.

Where  is a determination coefficient of an auxiliary regression model in which Xj is regressed against the other independent variables. The value of the VIF reflects the presence and severity of multicollinearity among the independent variables in the regression model. Reference [27] specifically discusses the use of VIF and some "rules of thumb" regarding its values. A VIF close to 1 suggests the absence of multicollinearity, while a VIF exceeding 10 indicates the presence of serious multicollinearity among the model variables, rendering the regression results unreliable.

Stepwise regression is a systematic algorithm for adding and removing terms from a multiple linear model based on their statistical significance in a regression, and is commonly used to correct the multicollinearity. This iterative procedure introduces independent variables into the regression model one by one to find the subset of the independent variable and corresponding regression coefficients that “best” explain the observations of the dependent variable. If the Xj independent variable meets the introduction criteria based on its significance, this new variable is introduced. Each time a new variable is introduced, the old variables of the selected equations are conducted T-test one by one. If the non-significant exclusion condition is met, the old variable is removed to ensure that the variables in the independent variable sub set are all significant. This process is repeated by several times until no new variables can be introduced [28].

C. Flow of the methodology proposal

Flow chart of the proposed method.

The location method for wiring fault user can be divided into two stages. The first stage is the data acquisition and preprocessing. In addition to measuring the target data of load current and residual current, multicollinearity tests are also conducted on these users. The second stage is model construction and analysis. The process specifically includes the following 5 steps:

Step1: For a LVDS serving multiple users, the amplitude data of the residual current and each user's load currents over a certain time should be collected to construct a sample set with a specified sampling rate when there arose an abnormal fluctuation in the residual current.

Step2: Preprocess the obtained current data and calculate the VIF for each user's load current to assess multicollinearity among user current data. If VIF is less than 10, proceed to step 4. Otherwise, go to step 3.

Step3: If there is multicollinearity among the users' load currents, the stepwise regression algorithm should be applied to filter out the optimal users' load current that are most strongly correlated with the abnormal residual current and are independent of each other.

Step4: Construct a MLR equation, solve the weight coefficients of each user's load current, and perform model validation.

Step5: Locate users with wiring fault based on the weight coefficients of the users' load current.

A detailed flow chart of the location method for wiring fault user is shown in Fig. 5.

Validation

In this paper, the electrical data of load current and residual current is collected to validate the effectiveness of the proposed method, three study cases with different scenario of wiring fault are presented based on the electricity safety simulation laboratory shown in Fig. 6.

Electricity safety simulation laboratory schematic diagram.

A TT grounding LVDS simulation laboratory that serving 80 low-voltage users, is used as an example LVDS to simulate a wiring fault scenario. The whole system consists of 8 user cabinet (simulating branch lines with multiple users), 7 line length cabinet (simulating the actual power supply distance between branch line), and a communication cabinet (uploading user metering data and giving control instructions). Meanwhile, the total residual current of the LVDS and the load current for each user are recorded for subsequent analysis. In this example LVDS, the voltage level of the transformer is 0.4kV, the transformer capacity is 400KVA, and adjustable loads are used to simulate the electricity consumption of the users.

The neutral line and the PE line of user 21 is set to be mis-wired in the user panel box when discussing the condition that there is only one anomaly user in the LVDS, and the user 1 and user 2 are set to suffer from wiring fault when discussing another condition that there are double anomaly users in the LVDS. The collected data of the load current of users and the residual current of the LVDS are recorded every 15 minutes within a day. And then those collected data is put into SPSS for MLR to locate wiring fault users.

A. Single User with Wiring Fault

As mentioned above, there is only one wiring fault user the user 21 in the simulated LVDS when the proposed method is applied to locate single user with wiring fault. According to Eq. (2), the residual current of the LVDS can be expressed as:

In general, users served by the same transformer have similar electricity behavior, so their load current fluctuation characteristics reflected a certain degree of similarity. Taking user 2 and user 4 as an example, their load current curves are shown in Fig. 7, where can be seen that two curves have a strong similarity in the fluctuation pattern. The electricity peak occurs from 6am~8am, 5pm~6pm, and 11 pm, which is also in accordance with lifestyle of residents.

Therefore, it is necessary to determine the VIF of each load current of users, and the calculation value is shown as APPENDIX TABLE A1, where most users in the simulated LVDS have severe multicollinearity trouble.

Load current of two user 2 and user 4.

To improve the reliability of the model, the time series of residual current is regarded as the dependent variable, which is denoted by symbol IR. The time series of load current of users 1~80 is regarded as the independent variable and denoted by symbol U1~80. The stepwise regression is applied to eliminate the independent variables causing multicollinearity trouble of the model and the optimal independent variables U17, U19, U21, U23, U28, U37 and U48 could be obtained. Taking these as independent variables and the time series of residual current of the LVDS as dependent variable, a new MLR model can be obtained as:

The goodness of fit test results for the new MLR model are presented in Table I, where the determination coefficient R2 is 1.000, and the standard error (Std-Error) is only 0.0094. This indicates that the new MLR model has an excellent reliability. Then setting the significance level of 0.05, the results of analysis variance showed that F=3779459.993, and the calculated result of the significance level (P) =0.000 ≤ 0.05. The analysis of variance (ANOVA) details are shown in Table II.

TABLE I

Goodness-of-fit test

| ### R | ### R2 | ### R2-Adjusted | ### Std-Error |
| --- | --- | --- | --- |
| ### 1.000 | ### 1.000 | ### 1.000 | ### 0.0094 |

TABLE II

ANOVA results of-MLR model

| Statistic | Sum of Squares | Degrees of Freedom | Mean square | F | P |
| --- | --- | --- | --- | --- | --- |
| Regression | 2351.064 | 7 | 335.866 | 37794 59.993 | 0.000 |
| Residuals | 0.008 | 88 | 0.000 | —— | — |
| Sum | 2351.072 | 95 | —— | —— | — |

The regression equation indicates a significant linear relationship between the independent variables included in the model and the residual current of the LVDS. This conclusion can be drawn after the successful F-test of the model.

After conducting a linear regression analysis in SPSS, the least square estimates of the regression coefficient for the optimal independent variables are presented in Table III. In addition, the T-test is also performed for each regression coefficients and the results are included in Table III.

TABLE III

T-test result of the optimal independent variables

| Variables | Non-Std Coefficient |  | Std-Coefficient | t | P |
| --- | --- | --- | --- | --- | --- |
|  |  | Std-Error |  |  |  |
| Constant | 0.023 | 0.002 | —— | 9.924 | 0.000 |
| U17 | 0.001 | 0.001 | 0.000 | 2.187 | 0.031 |
| U19 | -0.001 | 0.000 | -0.001 | -3.649 | 0.000 |
| U21 | 1.000 | 0.000 | 1.000 | 5027.699 | 0.000 |
| U23 | 0.000 | 0.000 | -0.001 | -2.712 | 0.008 |
| U28 | 0.001 | 0.000 | 0.001 | 3.167 | 0.002 |
| U37 | 0.000 | 0.000 | 0.000 | 1.953 | 0.054 |
| U48 | 0.001 | 0.000 | 0.001 | 4.181 | 0.000 |

According to the values shown in Table III, the MLR equation can be expressed as:

The T-test results indicate that the load current of these users has a significant impact on the residual current, with a significance level of 0.05. User 21 has a standardized coefficient value (Std-Coefficient) of 1.000, which is much higher than other users. It suggests that the time series of load current of user 21 has the greatest impact on the anomaly residual current, which implies that user 21 is wiring fault user, and it is consistent with the simulation settings.

B. Multiple-user with Wiring Fault

To further verify the ability of the proposed method to locate wiring faults in multi-user scenarios, MLR analyses is conducted on users with wiring faults in the same time. Same-phase and different-phase users with wiring fault are considered, and experimental data is used in the analysis. For simplicity, an example that double users with wiring faults is analyzed in this paper.

Case 1: Assuming that both user 1 and user 2 with wiring faults are connected in the same phase such as phase A. According to Eq. (3), the residual current of the LVDS can be expressed as

To eliminate multicollinearity trouble, the optimal explanatory variables U1, U2, U3, U6, U21, U23, U29, U32, U34, U42, U44, U55, and U60 are obtained by performing a stepwise regression analysis on the independent variables of the LVDS. Then, the auxiliary linear regression model is implemented, where the time series data of the residual current of the LVDS is regarded as the dependent variable and all of the optimal explanatory variables are regarded as independent variables.

TABLE IV

Regression coefficient in Same phase model

| Variables | Non-Std Coefficient |  | Std-Coefficient | t | P |
| --- | --- | --- | --- | --- | --- |
|  |  | Std Error |  |  |  |
| Constant | 0.043 | 0.001 | —— | 31.462 | 0.000 |
| U1 | 1.000 | 0.000 | 0.284 | 2578.123 | 0.000 |
| U2 | 1.000 | 0.000 | 0.975 | 8265.167 | 0.000 |
| U3 | -0.001 | 0.000 | -0.001 | -6.969 | 0.000 |
| U6 | 0.000 | 0.000 | 0.001 | 4.060 | 0.000 |
| U21 | 0.000 | 0.000 | 0.000 | 3.140 | 0.002 |
| U23 | 0.000 | 0.000 | -0.001 | -5.702 | 0.000 |
| U29 | 0.000 | 0.000 | 0.000 | -4.208 | 0.000 |
| U32 | 0.000 | 0.000 | 0.000 | 3.890 | 0.000 |
| U34 | 0.000 | 0.000 | 0.000 | 3.370 | 0.001 |
| U42 | 0.000 | 0.000 | 0.000 | 2.868 | 0.005 |
| U44 | -0.001 | 0.000 | 0.000 | -3.719 | 0.000 |
| U55 | 0.001 | 0.000 | 0.000 | 2.943 | 0.004 |
| U60 | 0.000 | 0.000 | 0.000 | -2.780 | 0.007 |

The goodness of fit test and variance analysis results for this model are presented in Appendix Table A2 and A3. The data shows that the adjusted determination coefficient R2 is 1.000, and the Std-Error is only 0.004, which demonstrates the excellent predictive capability of the optimal independent variables. At a significant level of 0.05, the model has passed the F-test, which indicates the effective overall linear relationship of the regression model. Once the linear regression calculations are completed in SPSS, the least square estimation of the regression coefficient for the optimal independent variables can be obtained as shown in Table IV. The significance of regression coefficients is also achieved by T test, and the results are displayed in Table IV.

Based on the data shown in Table IV, optimal independent variables of the load current have significant impact on the residual current of the LVDS, where the significance level is 0.05. The Std-coefficients of U1 and U2 carry more weight than other variables, and it suggests that both user 1 and user 2 have made significant contributions to the anomaly residual current of the LVDS. Furthermore, it can be observed that the Std-Coefficient of U1 is higher than that of U2. The reason is that the load current of the user 2 exhibits more intense fluctuations and consumes more electricity than the load current of the user 1. Therefore, user 1 and 2 are identified as the two wiring fault users, which is consistent with the simulation settings.

Case 2: If the two users are connected in different phases, assuming one is in Phase A and another is in Phase B, the residual current of the LVDS can be expressed as

The optimal independent variables U1, U2, U4, U11, U14, U17, U29, U55, U62, U66, U67, and U69 are selected by conducting a stepwise regression analysis on the metering data which is inputted into SPSS. Then the auxiliary MLR model is established with the dependent variables which are the time series of residual current of the LVDS, and all the aforementioned optimal explanatory variables are utilized as independent variables.

The goodness of fit test and variance analysis results of the model are presented in Appendix Table A4 and A5, where the adjusted determination coefficient R2 is 0.987 and the Std-Error is merely 0.477. It demonstrates that 98.7% of the total variation of residual current is explained by the estimated regression model. If the significance level is 0.05 and the F-test has passed with a calculated result of the significance level (P) = 0.000≤0.05, it denotes that the combination of independent variables included in the auxiliary model has a significant impact on the dependent variable. The regression coefficients for the optimal independent variables are estimated using least squares and the results are listed in Table V. Furthermore, the T-test is conducted for each regression coefficient and the results are also presented in Table V.

Table V

Regression coefficient in differ phase model

| Variables | Non-Std Coefficient |  | Std-Coefficient | t | P |
| --- | --- | --- | --- | --- | --- |
|  | ᵝ | Std Error | ᵝ |  |  |
| Constant | -0.722 | 0.197 | —— | -3.664 | 0.000 |
| U1 | 0.995 | 0.039 | 0.311 | 25.538 | 0.000 |
| U2 | 0.911 | 0.012 | 0.977 | 75.289 | 0.000 |
| U4 | -0.027 | 0.010 | -0.035 | -2.738 | 0.008 |
| U11 | 0.028 | 0.011 | 0.035 | 2.626 | 0.010 |
| U14 | 0.016 | 0.005 | 0.037 | 2.943 | 0.014 |
| U17 | -0.095 | 0.031 | -0.041 | -3.121 | 0.002 |
| U29 | -0.016 | 0.006 | -0.034 | -2.695 | 0.008 |
| U55 | -0.098 | 0.021 | -0.067 | -4.656 | 0.000 |
| U62 | 0.045 | 0.014 | 0.043 | 3.321 | 0.001 |
| U67 | -0.081 | 0.028 | -0.036 | -2.880 | 0.005 |
| U69 | -0.032 | 0.010 | 0.042 | -3.314 | 0.001 |

As illustrated in Table V, the load current of the optimal independent variables will affect the residual current at a significance level of 0.05. Notably, the absolute value of the Std-coefficients of U1 and U2 are much higher than the other variables, which means that both user 1 and user 2 have a significant effect on the anomaly residual current of the LVDS. The standard coefficients of U1 and U2 are slightly higher for users in different phases compared to those users in the same phase. It is worth noting that the difference in phase angle increased the similarity between the load current of the user and the anomaly residual current of the LVDS. Consequently, user 1 and user 2 are identified as wiring faults users, which is also consistent with the simulation settings.

Based on the analysis of scenarios involving single-user with wiring faults, double-users with wiring faults in the same phase, and double-users with wiring faults in different phases, the simulation results demonstrate the effectiveness of the proposed method in locating the users with wiring fault. As a result, the power utilities can implement targeted inspections on anomaly users based on the location results, which will enormously improve the efficiency of earth fault detection.

CONCLUSION

Wiring faults are commonly in LVDS. Unlike insulation failure associated earth faults, most traditional methods are not applicable to determine wiring faults. The composition of the residual current in the LVDS varies under different wiring fault scenarios. This paper proposes a method for the identification and localization of users with wiring faults based on MLR analysis, combined with metering data. This method can accurately distinguish and locate abnormal users in different wiring fault scenarios, thereby addressing a research gap in the current field of earth fault location. However, in practical engineering applications, factors such as data density, data quality, and the number of users can significantly affect the identification results. Additionally, due to the variety of earth fault types present in LVDS, more comprehensive and precise methods for the location and troubleshooting of earth faults still require further research.

APPENDIX A

Table A1

VIF of users

| User | VIF | User | VIF | User | VIF | User | VIF |
| --- | --- | --- | --- | --- | --- | --- | --- |
| X1 | 7.077 | X21 | 5.270 | X41 | 7.217 | X61 | 14.911 |
| X2 | 19.570 | X22 | 8.498 | X42 | 10.843 | X62 | 9.61 |
| X3 | 10.544 | X23 | 22.245 | X43 | 13.305 | X63 | 6.541 |
| X4 | 5.477 | X24 | 9.586 | X44 | 16.573 | X64 | 16.717 |
| X5 | 15.908 | X25 | 12.499 | X45 | 15.331 | X65 | 14.61 |
| X6 | 16.205 | X26 | 11.374 | X46 | 6.478 | X66 | 14.373 |
| X7 | 9.938 | X27 | 27.887 | X47 | 17.193 | X67 | 7.432 |
| X8 | 7.013 | X28 | 13.094 | X48 | 13.69 | X68 | 3.09 |
| X9 | 6.839 | X29 | 10.056 | X49 | 7.218 | X69 | 16.44 |
| X10 | 14.181 | X30 | 9.258 | X50 | 5.299 | X70 | 7.376 |
| X11 | 16.978 | X31 | 15.263 | X51 | 5.914 | X71 | 28.392 |
| X12 | 7.462 | X32 | 17.181 | X52 | 7.653 | X72 | 8.503 |
| X13 | 12.226 | X33 | 6.564 | X53 | 25.502 | X73 | 19.505 |
| X14 | 14.305 | X34 | 10.414 | X54 | 9.355 | X74 | 11.787 |
| X15 | 14.763 | X35 | 8.352 | X55 | 16.358 | X75 | 7.338 |
| X16 | 11.512 | X36 | 7.679 | X56 | 4.226 | X76 | 8.356 |
| X17 | 6.998 | X37 | 9.163 | X57 | 10.223 | X77 | 14.127 |
| X18 | 10.450 | X38 | 27.727 | X58 | 8.542 | X78 | 8.75 |
| X19 | 20.840 | X39 | 9.931 | X59 | 7.49 | X79 | 7.949 |
| X20 | 26.450 | X40 | 18.335 | X60 | 12.266 | X80 | 8.269 |

Table A2

In-phase model goodness of fit test

| R | R2 | R2-Adjusted | Std Error |
| --- | --- | --- | --- |
| 1.000 | 1.000 | 1.000 | 0.004 |

Table A3

In-phase model ANOVA results

| Statistic | Sum of Squares | Degrees of Freedom | Mean Square | F | P |
| --- | --- | --- | --- | --- | --- |
| Regression | 2032.835 | 13 | 156.372 | 7855873.187 | 0.000 |
| Residuals | 0.002 | 82 | 0.000 | — | — |
| Sum | 2032.837 | 95 | —— | — | — |

Table A4

Out-of-phase goodness of fit test

| R | R2 | R2-Adjusted | Std Error |
| --- | --- | --- | --- |
| 0.994 | 0.989 | 0.987 | 0.477 |

Table A5

Out-of-phase ANOVA results

| Statistic | Sum of Squares | Degrees of Freedom | Mean Square | F | P |
| --- | --- | --- | --- | --- | --- |
| Regression | 1664.414 | 11 | 151.310 | 664.284 | 0.000 |
| Residuals | 19.133 | 84 | 0.228 | —— | —— |
| Sum | 1683.547 | 95 | —— | —— | —— |

REFERENCES

H. Zhao, X. Xiao, Q. Sun, “Identifying electric shock in the human body via ɑ dispersion,” IEEE Trans. Power Del., vol. 33, no. 3, pp. 1107-1114, Jun. 2018.

Y. Liu, G. Liu, W. Sheng, S. Du, J. Wang, “An electric shock impedance modeling method of living organisms in low-voltage distribution network,” in Proc. IEEE China Int. Conf. Electricity Distrib., Xi'an, China, 2016, pp. 1-5.

N. Permal, M. Osman, M. Z. A. A. Kadir, A. M. Ariffin, “Review of substation grounding system behavior under high frequency and transient faults in uniform soil,” IEEE Access, vol. 8, pp. 142468-142482, Aug. 2020．

Y. M. Liu, S. H. Du, W. X. Sheng, “Classification and identification of electric shock current for safety operation in power distribution network,” IET Control. Theory Appl., vol. 5, no. 2, pp. 145-152. Jan. 2020．

X. Han, W. Sheng, S. Du, J. Su, G. Liu, “Novel protection scheme for residual current device-based electric fault time detection and touch current identification,” IET Gener. Transm. Distrib., vol. 11, no. 10, pp. 2478-2488, 2017.

H. Guan, M. Liu, C. L. Li, et al., “Classification recognition model of electric shock fault based on wavelet packet transformation and quantum neural network,” Trans. of the Chinese Society of Agricultural Engineering, vol. 34, no. 5, pp. 183-190, May. 2018.

G. Yang, S. Quan, W. Gao, “A new-designed biological electric shock identification method in low-voltage distribution network,” IEEE Trans. Power Del., vol. 38, no. 3, pp. 1558-1568, June. 2023.

C. L. Li, J. Wang, Z. Shi, C. Y . Wang, J. Luo, P . Ren, “Research on extraction method of electric shock current based on VMD-LSTM,” J.Hunan Univ. (Natural Sci.), vol. 49, no. 2, pp. 149–159, Feb. 2022.

J. Wang et al., “Spectrum analysis method of residual current based on Hilbert-Huang transform,” in Proc. IEEE Int. Conf. Probabilistic Methods Appl. Power Syst., Beijing, China, 2016, pp. 1-5.

Á. Espín-Delgado, J. Sutaria, S. Rönnberg, N. Nakhodchi, M. Bollen, “Impact of supraharmonics and quasi-DC on the operation of residual current devices,” IET Conf. Proc., vol. 2021, no. 6, pp. 668-672, 2021.

S. Czapp and K. Borowski, “Verification of safety in low-voltage power systems without nuisance tripping of residual current devices,” Electric Power Syst. Res., vol. 172, pp. 260–268, Jul. 2019．

K. Li et al., “A novel fault leakage current detection method with protection deadzone elimination,” IEEE Trans. Instrum. Meas., vol. 70, Art no. 3505009, pp. 1-9, Nov. 2021.

K. Li, C. Y. Xie, F. Niu, et al., “Modeling of residual current transformer considering nonlinear characteristics and design of output conditioning circuit parameters,” Proc. of the CSEE, vol. 42, no.10, pp. 3815-3826, 2022．

"Child hero saves entire building's inhabitants!": An electrician in Qingdao cracks a perplexing case, chilling details emerge accessed: Mar. 06, 2024. [Online]. Available: https://m.thepaper.cn/newsDetail _forward_25159549

A Heartbreaking Tragedy: Electrocution in the bathroom, Who is the culprit? accessed: Mar. 06, 2024. [Online]. Available: https:// www.sznews.com/news/content/2021-09/20/content_24585216.htm .

M. Orlando et al., “A smart meter infrastructure for smart grid iot applications,” IEEE Internet Things J., vol. 9, no. 14, pp. 12529-12541, July. 2022．

Y. Li, C.F. Xia, Z. Yuan, B.Q. Liao, S. Huang, “Research on residual current warning technology based on big data analysis,” J. of Physics: Conference Series(JPCS), vol. 2108, no.1, pp.012012, Nov. 2021.

K. Bhatia, P. B. Darji, H. R. Jariwala, “Safety analysis of TN-S and TN-C-S earthing system,” in Proc. IEEE Int. Conf. Environ. Electr. Eng., Palermo, Italy, 2018, pp. 1-6.

F. Freschi, “High-frequency behaviour of residual current devices,” IEEE Trans. Power Deliv., vol. 27, no. 3, pp. 1629–1635, Apr. 2012.

F. Möller, A. M. Blanco, J. Meyer, “Characteristic leakage current of household devices and their impact on the tripping behaviour of residual current devices,” Electr. Power Syst. Res., vol. 214, 108832, Jan. 2023.

J. Sutaria, A. Espin-Delgado, S. Rönnberg, “Measurements and modeling of the frequency behavior of residual current devices-from 4 Hz to 40 kHz,” Electr. Power Syst. Res., vol. 209, 108052, Aug. 2022.

Y. Wang, Q. Chen, T. Hong, C. Kang, "Review of Smart Meter Data Analytics: Applications, Methodologies, and Challenges," IEEE Trans. Smart Grid, vol. 10, no. 3, pp. 3125-3148, May 2019.

A. C. Sameepa Hettiarachchige-Don, V. Aravinthan, “Estimation of missing transmission line reactance data using multiple linear regression,” in Proc. North Amer. Power Symp., Morgantown, Morgantown, WV, USA, 2017, pp. 1-6.

H. H. Kenchannavar, P. M. Pujar, R. M. Kulkarni, U. P. Kulkarni, “Evaluation and analysis of goodness of fit for water quality parameters using linear regression through the internet-of-things-based water quality monitoring system,” IEEE Internet Things J., vol. 9, no. 16, pp. 14400-14407, Aug. 2022．

S. Kumar, S. Mishra, S. Gupta, “Short term load forecasting using ANN and multiple linear regression,” in Proc. 2nd Int. Conf. Comput. Intell. Commun. Technol. (CICT), Ghaziabad, India, 2016, pp. 184-186.

G. Kermarrec, A. Jain, S. Schön, “Kalman filter and correlated measurement noise: the variance inflation factor,” IEEE Trans. Aerosp. Electron. Syst., vol. 58, no. 2, pp. 766-780, Apr. 2022.

O’brien, R.M, “A caution regarding rules of thumb for variance inflation factors,” Qual Quant，vol. 41, pp. 673–690, Mar. 2007.

Y. Yi, S. Liu, Y. Zhang, Y. Xue, W. Deng, Q. Li, “Phase identification of low-voltage distribution network based on stepwise regression method,” J. Mod. Power Syst. Clean Energy, vol. 11, no. 4, pp. 1224-1234, Jul. 2023.