Fast and Reliable Detection of Synchronous Generator Loss of Excitation Using Rotor Speed Variation

Saman Soleymani1, Yousef Alinejad-Beromi1

1.Faculty of Electrical and Computer Engineering, Semnan University, Semnan, Iran

(E-mail: yalinejad@semnan.ac.ir)

Abstract:

Loss of Excitation (LOE) is one of the most critical faults in synchronous generators, which, if not detected promptly, can lead to power system instability and severe damage to the generator. The main challenge in distinguishing LOE from Stable Power Swings (SPS) lies in the time delay, which is a common issue in most recent protection methods. This paper presents a novel method for LOE detection in synchronous generators. The method utilizes a new criterion based on the variation of the generator rotor speed, where this criterion increases above one per unit after the occurrence of LOE and remains in this state. Unlike traditional methods that require complex settings, this approach operates without the need for threshold adjustments, ensuring accurate and fast performance under various conditions. In the simulations, generators of various sizes were subjected to various loads and network scenarios. The results of the simulations, which were carried out in MATLAB/Simulink, verify that the suggested approach not only diminishes the detection time but also preserves high accuracy when system disturbances occur, protecting system stability under severe conditions.

Keywords: synchronous generator, generator protection, loss of excitation detection, stable power swing

1-Introduction

In power systems, synchronous generators are essential for supplying electricity and maintaining network stability. Loss of Excitation (LOE) is a major problem with these generators. According to statistical studies, LOE is responsible for over 69% of all synchronous generator failures in China [1]. LOE in synchronous generators can occur due to an open or short circuit in the generator’s field winding. In the case of an open circuit, the field current abruptly drops to zero, whereas in a short circuit, the field voltage drops to zero. Because of this, the generator's internal voltage and reactive power output are significantly reduced, turning it into an induction generator that uses reactive power from the power system. The synchronous generator may experience mechanical failure, rotor heat damage, stator winding overload, and stator end-core damage as a result of the LOE [2][3][4]. Additionally, LOE can be partial, the partial LOE (PLOE) event occurs when the short-circuit phenomena take place in the fraction of this winding, which leads to a sudden drop of field voltage where the excitation is reduced but not entirely lost. Similar negative consequences, such heat damage to the rotor and stator and a voltage drop in the transmission lines, can even result from PLOE and have the potential to disrupt the power system. In order to preserve system stability, it is imperative that full LOE (CLOE) and PLOE be detected quickly [5][6]. Another important aspect of LOE detection is ensuring the accuracy of the method, especially under SPS conditions [3].

Various protective methods for LOE have been proposed. The oldest methods include using undercurrent relays connected to the field winding, which are not effective in distinguishing between a reduction in excitation and an accidental LOE [7]. Initially, Mason, in 1954, proposed measuring the impedance seen from the generator terminals to detect excitation loss based on its variations. He developed an idea that required using the generator's characteristics to plot an impedance circle on the R-X axis. Mason clarified that a problem is indicated if the impedance measured from the generator terminal enters and stays within the designated circular zone for a specific amount of time. Nevertheless, this approach has a number of shortcomings, including the potential for inaccuracies when subjected to high loads [8]. Mason's mistakes were successfully fixed in 1994 when Berdy proposed employing two distinct protection rings for light and heavy loads [9]. This strategy nonetheless had operational problems during SPS, in spite of its relative success [3].

New techniques for detecting LOE have emerged in recent years. For example, improvements have been suggested for three-phase reactive power[10], Artificial Neural Network(ANN) [11], and Adaptive Neuro Fuzzy Inference System (ANFIS) [12]. To improve LOE protection, fuzzy logic-based [13] methods and soft computing algorithms such as Decision Trees(DT) [14] and Support Vector Machines(SVM) [15] have been suggested for enhancing LOE protection. All of the aforementioned approaches however, rely on the system features and need a substantial quantity of data for training [10-14].

Other methods include the use of phasor measurements [16] and The flux-based method was introduced in [17][18] in which a search coil is used for flux measurement.

A combined scheme based on a derivative of the generator terminal voltage and output reactive power is proposed in [5], which exhibits mal-operation in the face of SPS. A setting-free method was presented in [19], which utilizes the rate of change of apparent resistance of the generator. In this reference, a time delay of 1.7 s is applied to prevent mal-operation against SPS condition. In [20] authors introduced the flux linkage-based method, in which the flux linkage is estimated using the other parameters of the generator. [21] proposed a novel approach to detect LOE events based on the generator's internal voltage parameter.

An algorithm based on the changes of some electrical quantities of the synchronous generator, such as terminal voltage, reactive power, and power angle, has been presented in [20] and then it is modified in [22]. Another method based on the generator armature current has been presented in [23], similar to the approach in [4], a delay of 1.7 seconds is incorporated to prevent maloperation. A new technique using field flux linkage and field current was put out in [24]. [25][26] have looked at how Flexible Alternating Current Transmission System (FACTS) devices affect LOE relays.

The second-order derivative of the generator's output reactive power stays positive for a few seconds after an LOE event, according to a new method for detecting LOEs. The study stressed how important it is to include a time delay in order to prevent mal-operation, especially when SPS is present. Interestingly, a novel technique for minimizing this time delay was incorporated into the suggested solution, bringing it into line with the slowest power swing conditions [27]. A study suggests a dynamic state estimation method for detecting LOE in synchronous machines, demonstrating improved accuracy and speed compared to impedance-based techniques [28].

A new method for detecting LOE based on a shaft speed variation index is presented in this paper. The suggested approach has been validated on a test network under a variety of situations through extensive simulations. The findings show that the suggested approach reliably separates LOE from SPS circumstances and offers the fastest LOE identification.

In the following sections, the proposed method is introduced and validated through both theoretical analysis and extensive simulations under various network conditions. The method's performance is then evaluated by simulating its application in both single-machine and multi-machine systems, where it is compared with existing methods in terms of effectiveness and reliability. The paper concludes with a summary of findings and offers recommendations for future research.

2-PROPOSED METHOD

1-Studied system

The power grid under study is typically modeled as a single machine connected to an infinite bus through transmission lines, that is widely used by authors of technical books [3], and researchers [17]-[28] as shown in Figure 1. The single-machine infinite-bus system (SMIB) model serves to validate the generator state estimator and LOE fault detection algorithm. The system is simulated in MATLAB to estimate the generator's state variables and analyze their behavior during an LOE event. This approach is favored because the simulated system’s response to disturbances or faults closely matches the signals observed during real power swings.  The simulation is conducted with a time step of 100 microseconds. The generator in the study has a terminal voltage of 13.8 kV and a power rating of 390 MVA, while the short-circuit capacity (SCC) of the external grid connected to the generator is set at 100,000 MVA.

2-Strategy concept

One of the key parameters influenced by LOE is rotor speed. In the event of such a LOE, the mechanical input power surpasses the electrical power, resulting in an increase in rotor speed [7]. Research on the effects of LOE has demonstrated that the generator speed does not revert to its pre-fault value. Instead, it tends to oscillate above this value until the fault is either correct or the system loses of synchronism (LOS) and transitions into instability.

One of the equations used in generator modeling pertains to the dynamic modeling of the rotor. According to [22]:

| (1) | d2δtdt2=πfsHPm-P |
| --- | --- |
| (2) | ∆δt∆t=ωt-ωs |

In this context, H(s) fs(Hz), Pm(pu), P(pu), and ω denote the inertia constant, synchronous frequency, mechanical input power, electrical output power, and rotor speed, respectively. Integrating of (1) over ∆t yields:

| (3) | t-∆ttd2δtdt2dt=πfsHt-∆ttPm-Pdt |
| --- | --- |

From the right-hand of the (3) and use (2):

| (4) | dδdtt-dδdtt-c=ωt-ωs-ωt-∆t-ωs=ωt-ωt-∆t |
| --- | --- |

On the right-hand of the equality in equation (3), assuming that the mechanical input power is constant at the moment of the LOE and does not change:

| (5) | πfsH(Pm-P)t+(Pm-P)t-∆t2×∆t=πfsH2Pm-Pt-Pt-∆t2 |
| --- | --- |

From equations (4) and (5), it follows that:

| (6) | ωt-ωt-∆t=πfsH2Pm-Pt-Pt-∆t2 |
| --- | --- |
| (7) | ωt=ωt-∆t+πfsH2Pm-Pt-Pt-∆t2 |

Upon the occurrence of an LOE, the electrical output power, which comprises both active and reactive components, experiences a decline. This decline manifests as oscillatory and damped behavior. Depending on the generator and grid conditions, the system may remain in this state for a period of time [2]. Consequently, the rate of change in speed over a time interval ∆t is consistently positive, resulting in the rotor speed remaining above the synchronous speed. According to Equation (7), the speed is also dependent on the generator's inertia coefficient, which is a fixed value for a given generator and is determined by the generator's size.

In most of the proposed methods, distinguishing between LOE and other faults and SPS has been of paramount importance. Therefore, it is essential to examine how rotor speed changes during SPS and other types of faults to identify and differentiate the patterns of these variations.

Figure 1: single-machine-infinite bus (SMIB) system[13]

As shown in Figure 2, the per unit (pu) rotor speed of the generator during an SPS in an SMIB system, which corresponds to (9), has been simulated using MATLAB/Simulink [19].

| (8) | ωrotort=1+k.e-tτ.sin2πfslip.t+α |
| --- | --- |

Here, α and k are constants, τ​ represents the damping time constant of the speed profile, and fslip​ denotes the slip frequency, which corresponds to the frequency of rotor speed variations. Typically, this frequency falls within the range of 0.3 to 7 Hz [19]. In this study, to evaluate the worst-case scenario or the slowest power oscillations, we assume an oscillation frequency of 0.3 Hz. Thus, the longest period of speed rotor that can be expected during a power swing is 10.3 =3.33 seconds, The resulting speed profile during power oscillations is illustrated by the following Figure 2:

Figure 2: Oscillations of the speed rotor during the slowest power swing

However, in the proposed scheme, which operates with rotor speeds greater than one per unit, it is necessary to detect when the speed exceeds one per unit. To achieve this, only half of this period is required. According to the fig 2, the half-period of oscillation is approximately 1.667 seconds. For this study and to ensure reliability, this value is considered as 1.7 seconds. In other words, a time delay of 1.7 seconds is needed to distinguish LOE faults from SPS and another type of faults.

As demonstrated in Fig. 3, it is observed that after the occurrence of an LOE, the rotor speed, despite the presence of control feedback mechanisms, never returns to one per unit. The main causes of this ongoing deviation are the generator's mechanical modes, which are impacted by its damping and inertia properties, as well as the governor's transient response [2]. All of these elements work together to make it challenging to stabilize rotor speed after the fault.

Extensive simulations have shown that whenever the rotor speed reaches its second main extremum without returning to one per unit, it indicates an LOE. To accurately identify this second main relative extremum above one per unit, it is necessary to eliminate noise present in the signal, which may be caused by mechanical noise in the shaft and the system's inability to dampen SPS effectively. Initially, noise in the rotor speed signal is filtered out using a low-pass filter. The first derivative of the low-pass filtered signal is then computed. As shown in Fig. 3 the zero crossings of the first derivative indicate the relative extrema.

Figure 3: Detect the main extrema in the changes in rotor speed

In this method, the speed is continuously compared to the one per-unit value An LOE is considered to have occurred if the speed is greater than one per unit and the number of relative extrema reaches two. After an LOE, the rotor may experience first-swing instability, which can cause a continuous increase in speed without forming a relative extremum, eventually leading to a LOS. To address this, the method includes a 1.7-second time delay constraint. The risk of first-swing instability depends on the network size connected to the generator and also the size of the generator.

Based on these explanations, the algorithm for the proposed method is illustrated in Fig. 4.

Figure 4: Flowchart of the proposed method.

3-Simulation and Evaluation

Generators of various sizes were examined under various loading circumstances in a SMIB system, exposed to both CLOE and PLOE scenarios, in order to produce thorough simulations. The effects of deviations from the infinite bus must also be investigated, and the system should eventually be assessed in the presence of three-phase short circuit faults and SPS conditions.

1-Impacts of CLOE and PLOE on the proposed method

For PLOE simulations, the excitation field (Ef) was set to 0.3 pu and 0.6 pu, while for CLOE, Ef= 0. As shown in Fig. 5 and Table 1 the proposed method detects PLOE more quickly. However, CLOE leads to a faster LOS, with a sharper increase in rotor speed, compared to the delayed LOS seen in PLOE.

Figure 5: LOE detection for CLOE and PLOEs.

2-Impacts of generator size on the proposed method

The suggested approach greatly improves the detection of LOE, especially in smaller generators, according to simulations performed on generators of various sizes under constant loading conditions. Even under the same loading conditions, the results demonstrate that smaller generators detect LOE more quickly than larger units, as shown in Figure 6. Equation (7) indicates that the generator's response time is significantly influenced by the inertia coefficient (H). Typically, larger generators have higher inertia values, resulting in slower fault detection. However, exceptions exist, such as the 390 MVA unit, despite its size, has a relatively larger inertia coefficient (H = 5.5 sec). Specifically, the sequence of LOE detection, ordered by increasing inertia coefficient (H), is as follows: 80 MVA (H = 3.5 s), 500 MVA (H = 4 s), 600 MVA (H = 4.4 s), and 390 MVA (H = 5.5 s). The data supporting these observations are summarized and analyzed in Table 1.

Figure 6: LOE detection for different sizes of generator

4- Impacts of loads on the proposed method

An SMIB system was subjected to a number of simulations in both light and heavy loading scenarios, that includes resistive-inductive and resistive-capacitive loads. Under these circumstances, the proposed method for identifying LOE was used. As illustrated in Figure 7, the method demonstrated superior performance in detecting LOE more rapidly under resistive-inductive loading compared to resistive-capacitive loading Additionally, the technique demonstrated greater efficacy when subjected to light resistive-inductive loading as opposed to heavy resistive-inductive loading. A similar trend was observed for resistive-capacitive loads.

Figure 7: LOE detection for different loads

5- Impacts of grid

As seen in Figure 1, an infinite bus with clearly defined characteristics is connected to the generator in a SMIB system. However, during faults and SPS, the network capacity linked to the generator is essential for reducing oscillations and avoiding LOS. To clearly demonstrate this effect, simulations were conducted with networks of both very large and very small capacities to assess the impact of network power on the proposed method. Figure 8 shows the rotor speed variations of a generator connected to networks with different 3-phase short-circuit levels (SCL) at base voltage. This topic is also addressed in Table 1, specifically in cases 1, 2, 11, and 12.

Figure 8: different sizes of SCL

As evident, the frequency of speed oscillations increases as the SCL of the network connected to the system grows, leading to the faster formation of relative extrema. In other words, the more robust the network to which a synchronous generator is connected during an LOE, the quicker its response.

Table 1: performance of the proposed method during LOE events in the SMIB system

| Case | Generator power (MVA) | Initial loading |  | Network SCL (MVA) | Ef = 0 (pu) | Ef = 0.3 (pu) | Ef = 0.6 (pu) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | P (pu) | Q (pu) |  |  |  |  |
| 1 | G1= 80 | 0.85 | 0.28 | 845000 | 0.6533 | 0.6524 | 0.6512 |
| 2 | G1= 80 | 0.285 | 0.093 |  | 0.6608 | 0.6597 | 0.6584 |
| 3 | G2=210 | 0.85 | 0.28 |  | 1.1879 | 1.1948 | 1.1998 |
| 4 | G2=210 | 0.285 | 0.093 |  | 1.1781 | 1.1879 | 1.1940 |
| 5 | G2= 390 | 0.85 | 0.28 |  | 0.9168 | 0.9153 | 0.9137 |
| 6 | G2= 390 | 0.285 | 0.093 |  | 0.9201 | 0.9187 | 0.9172 |
| 7 | G3=600 | 0.85 | 0.28 |  | 0.7927 | 0.7888 | 0.7828 |
| 8 | G3=600 | 0.285 | 0.093 |  | 0.7877 | 0.7840 | 0.7775 |
| 9 | G1= 80 | 0.76 | 0.25 |  | 0.6551 | 0.6540 | 0.6528 |
| 10 | G1= 80 | 0.76 | -0.25 |  | 0.6717 | 0.6702 | 0.6690 |
| 11 | G1= 80 | 0.85 | 0.28 | 100000 | 0.6572 | 0.6561 | 06549 |
| 12 | G1= 80 | 0.285 | 0.093 |  | 0.6650 | 0.6639 | 0.6626 |

6-Simulation SPS condition

To validate the proposed method, simulations were performed on an SMIB subjected to typical power fluctuations, including heavy load events (0.8+j0.4) and a 200 ms three-phase short circuit. As demonstrated in Figure 9, the method did not falsely trigger in response to these disturbances, the control feedback system effectively restores rotor speed to one per unit within 1.7 seconds, with all primary relative minima occurring below one per unit. In contrast, conventional methods exhibit mal-operation under SPS conditions [4], [20], [27].

Figure 9: a) Three-phase short-circuit with a duration of 200 ms b) Heavy load (0.8+j0.4) injection and rejection events

4-Comparative analysis and discussion:

This section compares the suggested method to earlier techniques for the SMIB system under a range of load conditions. The suggested approach demonstrated noticeably quicker LOE detection than traditional techniques, as indicated in Table 2. The recommended approach consistently achieved superior detection speed, identifying faults within less than one second in all tested scenarios, as shown by Table 3, which also compares it with other previously suggested techniques.

TABLE 2:  A Comparison of the mentioned approach and the impedance-based method in the SMIB system

| Case | Initial loading |  | Time detection |  |
| --- | --- | --- | --- | --- |
|  | P (pu) | Q (pu) | Conventional method(s) [9] | Proposed method(s) |
| 1 | 0.95 | 0.42 | 4.274 | 0.9142 |
| 2 | 0.9 | -0.26 | 2.935 | 0.9243 |
| 3 | 0.7 | -0.37 | 2.708 | 0.9255 |
| 4 | 0.6 | 0.18 | 4.720 | 0.9236 |
| 5 | 0.5 | -0.13 | 4.147 | 0.9230 |
| 6 | 0.4 | 0.06 | 5.053 | 0.9205 |
| 7 | 0.3 | -0.15 | 4.755 | 0.9233 |
| 8 | 0.1 | 0.15 | 6.468 | 0.9193 |

TABLE 3: Performance of different methods during LOE event in the SMIB system

| Detection time in proposed method (sec) | Detection time in reference (sec) | Initial loading (pu) | Reference number |
| --- | --- | --- | --- |
| 0.9168 | 1.831 | 0.85+J0.28 | [22] |
| 0.9270 | 1.831 | 0.76-J0.25 | [22] |
| 0.9212 | 1.022 | 0.57+J0.18 | [4] |
| 0.9228 | 1.025 | 0.28+J0.09 | [4] |
| 0.9188 | 3.22 | 0.9+J0.3 | [18] |
| 0.9285 | 3.1 | 0.5-J0.4 | [18] |
| 0.9286 | 4.3 | 0.3-J0.4 | [21] |
| 0.9175 | 2.9 | 0.3+J0.4 | [21] |
| 0.9153 | 1.1 | 0.7+J0.5 | [27] |
| 0.9193 | 1.2 | 0.2-J0.3 | [27] |
| 0.9168 | 1.251 | 0.85+j0.28 | [28] |

Finally, to further validate the effectiveness of the proposed method, it was applied to a Multi-Machine Infinite Bus (MMIB) network, as depicted in Figure 10 and assessed under various scenarios involving LOE fault. The performance of  generator G2 was evaluated based on the findings presented in [27]. Even in the MMIB, the results in Table 4 show that the suggested method consistently identified LOE in less than one second, demonstrating superior detection speed when compared to alternative approaches.

Figure 10: Simulated MMIB system [18]

Table 4. Performance of different methods during LOE event in the MMIB system

| Proposed method (sec) | [27] (sec) | [22] (sec) | [4] (sec) | Conventional (sec)[9] | Initial loading (pu) |  |  | Case |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | G3 | G2 | G1 |  |
| 0.8955 | 1.102 | 1.831 | 1.021 | 4.897 | 0.8+j0.4 | 0.8+j0.4 | 0.8+j0.4 | 1 |
| 0.8890 | 1.104 | 1.831 | 1.021 | 8.389 | 0.3+j0.1 | 0.5+j0.3 | 0.8+j0.4 | 2 |
| 0.8967 | 1.108 | 1.831 | 1.023 | 15.501 | 0.8+j0.4 | 0.3+j0.1 | 0.5+j0.3 | 3 |
| 0.9072 | 1.178 | 1.831 | 1.046 | 3.532 | 0.7-j0.4 | 0.7-j0.3 | 0.5+j0.3 | 4 |
| 0.8976 | 1.18 | 1.831 | 1.078 | 4.390 | 0.6+j0.4 | 0.5-j0.4 | 0.5-j0.3 | 5 |

Subsequently, the MMIB system was subjected to power fluctuations caused by the injection and rejection of heavy loads, as well as three-phase short circuits of varying durations on different lines. As shown in Table 5, the conventional method incorrectly triggered a G3 trip command in scenarios 2 and 3, while the  [4] method mal-operated in both Scenarios 2 and 4. In contrast, the proposed method demonstrated no errors across all scenarios, further underscoring its reliability.

Table 5. Comparison of Method Performance During SPS Scenarios in an MMIB System

| Proposed method | [27] | [22] | [4] | Conventional method[9] | Ts (ms) | SPS event | Initial loading(pu) |  |  | Case |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | G3 | G2 | G1 |  |
| No trip | No trip | No trip | No trip | No trip | 230 | Sc on line 1 | 0.7+j0.4 | 0.7-j0.2 | 0.6-j0.3 | 1 |
| No trip | No trip | No trip | Trip at t= 2.048 | Trip at t= 2.356 | 350 | Sc on line 7 | 0.3-j0.4 | 0.8+j0.4 | 0.7+j0.3 | 2 |
| No trip | No trip | No trip | No trip | Trip at t= 2.291 | 150 | Sc on line 5 | 0.8-j0.5 | 0.7+j0.2 | 0.8-j0.5 | 3 |
| No trip | No trip | No trip | Trip at t= 2.567 | No trip | 250 | Sc on line 5 | 0.8+j0.4 | 0.6+j0.3 | 0.7+j0.3 | 4 |
| No trip | No trip | No trip | No trip | No trip | No trip | Ejection of Loads 1 and 2 | 0.8+j0.4 | 0.8+j0.4 | 0.8+j0.4 | 5 |
| No trip | No trip | No trip | No trip | No trip | No trip | Switching of Loads 1 and 2 | 0.8+j0.4 | 0.8+j0.4 | 0.8+j0.4 | 6 |

5-Conclusion

This paper presents a novel method for detecting LOE conditions in synchronous generators by precisely analyzing the generator shaft speed signal, which significantly reduces fault detection time. This method outperforms the conventional approach in terms of LOE detection speed and accuracy, as shown by extensive simulations in both SMIB and MMIB systems. For instance, the detection time for a 360 MW generator experiencing an LOE fault under a load of 0.95 + j0.42 has been reduced from 4.274 seconds using the impedance-based method to 0.9142 seconds using the suggested method. Furthermore, this method works well in complex scenarios like SPS and short-circuit faults and shows excellent stability under a range of grid conditions. The proposed method provides fast and reliable protection without dependency on transient generator parameters, ensuring timely generator tripping and preventing prolonged outages.

References

[1]	Z. P. Shi, J. P. Wang, Z. Gajic, C. Sao, and M. Ghandhari, “The comparison and analysis for loss of excitation protection schemes in generator protection,” in IET Conference Publications, 2012. doi: 10.1049/cp.2012.0071.

[2]	D. Reimert, “Protective Relaying for Power Generation Systems,” Prot. Relaying Power Gener. Syst., pp. 1–561, Dec. 2017, doi: 10.1201/9781420030488/PROTECTIVE-RELAYING-POWER-GENERATION-SYSTEMS-LEE-WILLIS-DONALD-REIMERT/ACCESSIBILITY-INFORMATION.

[3]	“C37.102-2006 - IEEE Guide for AC Generator Protection | IEEE Standard | IEEE Xplore.” Accessed: Sep. 02, 2024. [Online]. Available: https://ieeexplore.ieee.org/document/8526571

[4]	M. Amini, M. Davarpanah, and M. Sanaye-Pasand, “A novel approach to detect the synchronous generator loss of excitation,” IEEE Trans. Power Deliv., vol. 30, no. 3, 2015, doi: 10.1109/TPWRD.2014.2370763.

[5]	M. Elsamahy, S. O. Faried, and T. Sidhu, “Impact of midpoint STATCOM on generator loss of excitation protection,” IEEE Trans. Power Deliv., vol. 29, no. 2, pp. 724–732, 2014, doi: 10.1109/TPWRD.2013.2281581.

[6]	H. Yaghobi, “Out-of-step protection of generator using analysis of angular velocity and acceleration data measured from magnetic flux,” Electr. Power Syst. Res., vol. 132, pp. 9–21, Mar. 2016, doi: 10.1016/J.EPSR.2015.11.003.

[7]	P. Kundur, “Power System Stability and Control - Prabha Kundur - McGraw-Hill Education,” p. 1176, 1994, Accessed: Sep. 02, 2024. [Online]. Available: https://www.mheducation.co.in/html/9780070635159.html

[8]	C. R. Mason, “A New Loss-of-Excitation Relay for Synchronous Generators,” Trans. Am. Inst. Electr. Eng., vol. 68, 1949, doi: 10.1109/T-AIEE.1949.5060079.

[9]	J. Berdy, “Loss of excitation protection for modern synchronous generators,” IEEE Trans. Power Appar. Syst., vol. 94, no. 5, 1975, doi: 10.1109/T-PAS.1975.31987.

[10]	M. H. Musa M Bayrak Ma Redfern, O. Usta, M. H. Musa, M. Bayrak, and M. A. Redfern, “A New Relaying Algorithm to Detect Loss of Excitation of Synchronous Generators,” Turkish J. Electr. Eng. Comput. Sci., vol. 15, no. 3, pp. 339–349, Jan. 2007, doi: -.

[11]	A. M. Sharaf and T. T. Lie, “ANN based pattern classification of synchronous generator stability and loss of excitation,” IEEE Trans. Energy Convers., vol. 9, no. 4, 1994, doi: 10.1109/60.368331.

[12]	M. S. A. Aziz, M. Elsamahy, M. A. M. Hassan, and F. Bendary, “Loss of excitation detection in hydro-generators based on ANFIS approach using positive sequence components,” in Proceedings of the 19th International Conference on Soft Computing and Measurements, SCM 2016, 2016. doi: 10.1109/SCM.2016.7519765.

[13]	A. P. De Morais, G. Cardoso, and L. Mariotto, “An innovative loss-of-excitation protection based on the fuzzy inference mechanism,” IEEE Trans. Power Deliv., vol. 25, no. 4, 2010, doi: 10.1109/TPWRD.2010.2051462.

[14]	T. Amraee, “Loss-of-field detection in synchronous generators using decision tree technique,” IET Gener. Transm. Distrib., vol. 7, no. 9, 2013, doi: 10.1049/iet-gtd.2013.0138.

[15]	E. Pajuelo, R. Gokaraju, and M. S. Sachdev, “Identification of generator loss-of-excitation from power-swing conditions using a fast pattern classification method,” IET Gener. Transm. Distrib., vol. 7, no. 1, 2013, doi: 10.1049/iet-gtd.2012.0340.

[16]	T. Bi, J. Sui, H. Yu, and Q. Yang, “Adaptive loss of field protection based on phasor measurements,” IEEE Power Energy Soc. Gen. Meet., 2011, doi: 10.1109/PES.2011.6039170.

[17]	H. Yaghobi and H. Mortazavi, “A novel method to prevent incorrect operation of synchronous generator loss of excitation relay during and after different external faults,” Int. Trans. Electr. Energy Syst., vol. 25, no. 9, pp. 1717–1735, Sep. 2015, doi: 10.1002/ETEP.1922.

[18]	H. Yaghobi, H. Mortazavi, K. Ansari, H. R. Mashhadi, H. K. Zadeh, and H. Borzoe, “Study on application of flux linkage of synchronous generator for loss of excitation detection,” Int. Trans. Electr. Energy Syst., vol. 23, no. 6, pp. 802–817, Sep. 2012, doi: 10.1002/ETEP.1626.

[19]	B. Mahamedi, J. G. Zhu, and S. M. Hashemi, “A setting-free approach to detecting loss of excitation in synchronous generators,” IEEE Trans. Power Deliv., vol. 31, no. 5, pp. 2270–2278, Oct. 2016, doi: 10.1109/TPWRD.2015.2504539.

[20]	A. Hasani and F. Haghjoo, “Fast and secure detection technique for loss of field occurrence in synchronous generators,” IET Electr. Power Appl., vol. 11, no. 4, 2017, doi: 10.1049/iet-epa.2016.0551.

[21]	M. Abedini, M. Sanaye-Pasand, and M. Davarpanah, “An Analytical Approach to Detect Generator Loss of Excitation Based on Internal Voltage Calculation,” IEEE Trans. Power Deliv., vol. 32, no. 5, 2017, doi: 10.1109/TPWRD.2016.2616386.

[22]	A. Hasani and F. Haghjoo, “A Secure and Setting-Free Technique to Detect Loss of Field in Synchronous Generators,” IEEE Trans. Energy Convers., vol. 32, no. 4, 2017, doi: 10.1109/TEC.2017.2697501.

[23]	N. Noroozi, H. Yaghobi, and Y. Alinejad-Beromi, “Analytical technique for synchronous generator loss-of-excitation protection,” IET Gener. Transm. Distrib., vol. 11, no. 9, 2017, doi: 10.1049/iet-gtd.2016.1494.

[24]	M. Abedini, M. Sanaye-Pasand, M. Davarpanah, and R. Iravani, “A Loss-of-Field Detection Relay Based on Rotor Signals Estimation,” IEEE Trans. Power Deliv., vol. 33, no. 2, 2018, doi: 10.1109/TPWRD.2017.2718839.

[25]	A. Ghorbani, B. Mozafari, S. Soleymani, and A. M. Ranjbar, “Operation of synchronous generator LOE protection in the presence of shunt-FACTS,” Electr. Power Syst. Res., vol. 119, 2015, doi: 10.1016/j.epsr.2014.09.019.

[26]	H. Yaghobi, “Impact of static synchronous compensator on flux-based synchronous generator loss of excitation protection,” IET Gener. Transm. Distrib., vol. 9, no. 9, 2015, doi: 10.1049/iet-gtd.2014.0859.

[27]	N. Noroozi, Y. Alinejad-Beromi, and H. Yaghobi, “Fast approach to detect generator loss of excitation based on reactive power variation,” IET Gener. Transm. Distrib., vol. 13, no. 4, 2019, doi: 10.1049/iet-gtd.2018.5049.

[28]	E. Momeni, H. Yaghobi, and A. Shahzadi, “Using dynamic state estimation to detect loss of excitation in synchronous generators,” IET Gener. Transm. Distrib., vol. 18, no. 3, 2024, doi: 10.1049/gtd2.13106.

[29]	M. Abedini, M. Sanaye-Pasand, and M. Davarpanah, “Flux linkage estimation based loss of excitation relay for synchronous generator,” IET Gener. Transm. Distrib., vol. 11, no. 1, 2017, doi: 10.1049/IET-GTD.2016.1009.

APPENDIX  I

Generators parameters

|  | S MVA | V kv | Xd pu | Xq pu | Xd' pu | Xq' pu | Xd" pu | Xq" pu | Tdo' s | Tdo" s | Tqo" s | H s |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G1 | 80 | 13.8 | 0.9 | 0.54 | 0.3 | 0.65 | 0.24 | 0.25 | 5.4 | 0.03 | 0.09 | 3.5 |
| G2 | 390 | 13.8 | 1.2 | 0.7 | 0.3 | 0.65 | 0.18 | 0.17 | 5 | 0.1 | 0.09 | 5.5 |
| G3 | 500 | 13.8 | 1.6 | 0.97 | 0.48 | 0.65 | 0.3 | 0.25 | 6.1 | 0.1 | 0.18 | 4 |
| G4 | 600 | 13.8 | 1.81 | 1.76 | 0.3 | 0.65 | 0.23 | 0.25 | 8 | 0.03 | 0.07 | 4.4 |
| G5 | 210 | 13.8 | 2.11 | 1.91 | 0.268 | 0.434 | 0.21 | 0.18 | 0.635 | 0.015 | 0.18 | 14.688 |

Exciter and AVR parameters:

| Tc | Tb | Te | Ke | Ta | Ka | Tr |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 1 | 0.001 | 300 | 0.02 |
| Vf0 | Vt0 | Kp | Efmax | Efmin | Tf | Kf |
| 1 | 1 | 0 | +11.5 | -11.5 | 0.1 | 0.001 |

Transformers parameters:

| Generator |  | Transformer |  |  |
| --- | --- | --- | --- | --- |
|  | S MVA | VL kv | VH kv | T MVA |
| G1 | 80 | 13.8 | 400 | 80 |
| G2 | 390 | 13.8 | 400 | 400 |
| G3 | 500 | 13.8 | 400 | 500 |
| G4 | 600 | 13.8 | 400 | 600 |
| G5 | 210 | 13.8 | 400 | 210 |

Transmission lines parameters:

| MMIB |  | SMIB |
| --- | --- | --- |
| L1 | 0.048+j0.48 Ωkm | 0.061+j0.277 Ωkm |
| L2 | 0.00576+j0.573 Ωkm | 0.061+j0.277 Ωkm |
| L3 | 0.0288+j0.288 Ωkm | - |
| L4 | 0.0576+j0.576 Ωkm | - |
| L5 | 0.0142+j0.142 Ωkm | - |
| L6 | 0.00192+j0.192 Ωkm | - |
| L7 | j0.0957 Ωkm | - |