Development of Economical Hardware Enhancement for Load Break Switch in Smart Distribution Network

Praditpong Suksirithawornkul1, Teratam Bunyagul1, Noppadol Charbkaew1,*, Yotaka Chompusri1, Tirapong Kasirawat2, Narong Tantichayakorn2

1Department of Electrical and Computer Engineering, King Mongkut's University of Technology North Bangkok,

Bangkok, 10800, Thailand
2Provincial Electricity Authority, Bangkok, 10900, Thailand

*Corresponding author: Noppadol Charbkaew (noppadol.c@eng.kmutnb.ac.th)

Abstract: This study explores the design and evaluation of an economical hardware platform aimed at enhancing load break switches (LBS) in distribution systems. Simulations conducted using DIgSILENT Power Factory and PSCAD validated the proposed method. The Provincial Electricity Authority of Chiang Mai Province successfully implemented this hardware platform in the Ban Khun Pae Smart Microgrid project. The hardware platform underwent rigorous laboratory testing using an overcurrent algorithm to detect fault currents. It successfully identified all potential issues, including saturation currents on feeders, and autonomously transmitted data to operators for timely corrective action. The findings confirmed that single line-to-ground fault currents were the most frequent fault type. The Intelligent Electronic Devices relay and the InHand Wireless Overhead-Line System fault current detectors at the site worked just as well as the improved LBS, showing that they are strong and reliable ways to find faults. This economical and efficient platform not only enhances operational reliability but also paves the way for improved fault monitoring and management in distribution systems, ensuring faster response times, and minimizing downtime during faults.  The seamless integration with existing feeder infrastructure further highlights its practical utility and scalability, providing an innovative solution to the challenges faced in modern distribution networks.

Keywords: distribution networks, hardware platform, load break switch, power distribution faults, power system faults

# NOMENCLATURE

ACRONYMS

ADC	Analog to digital converter

ANN	Artificial neural networks

API	Application Programming Interface

CT	Current transformer

CPU	Central processing unit

DWT	Discrete wavelet transform

FRTUs	Feeder remote terminal units

FPGAs	Field programmable gate arrays

FCN	Fully convolutional network

FCDFT	Full-cycle discrete Fourier transform

FCN	Fully Convolutional Network

IEDs	Intelligent electronic devices

IWOS	InHand Wireless Overhead-Line System

I/O	Input / Output

HCDFT	Half-cycle discrete Fourier transform

HMI	Human machine interface

HTTPS	Hypertext transfer protocol secure

LBS	Load break switch

MCU	Microcontroller unit

MFL	Magnetic flux leakage

MSF	Magnetic field sensor

PEA	The Provincial Electricity Authority

PLC	Programmable logic controller

PS	Partial saturation

PSO	Particle swarm optimization

SDOFP	Short data window orthogonal filter pair

SVR	Support vector regression

TDMS	The transmission and distribution management systems

UKF	Unscented Kalman filter

UWLS	Unconstrained weighted-least squares

SYMBOLS

A	Current ampacity

H	Henry

Hz	Frequency

V	Voltage magnitude

$	US dollar

VARIABLES

∅s(k)	First filter.

∅c(k)	Second filter.

∆t	A sampling period.

L	Length of period.

γ_S	The impulse response of the sinusoidal.

γ_C	Cosine filters at the fundamental frequency.

a(n)	The real magnitude of signal.

b(n)	The imaginary magnitude of signal.

I_1 (n)	The signal current.

i(n)	The instantaneous signal current

∆I(n)	The absolute value of the rate of change in magnitude.

θ(n)	The angle-of-change rate of the signal.

∆θ(n)	The rate of change.

ω_0	The fundamental frequency.

# 1.Introduction

The CT may saturate when utilizing too small CT or a secondary load with a high burden. Excessive saturation of the CT may lead to the distortion of the secondary current. Consequently, the relay could detect a distorted secondary current that does not accurately reflect the real fault current. This might impact the duration of operation and lead to problems in a time-graded protection system. The online fault detection system integrated into the saturation detector could accurately detect fault current events and record them on the same day and time as the IEDs relay installed in the project.  The FRTU upgrade also enabled efficient fault detection in the distribution system, providing reliability comparable to newer FRTUs with higher costs and relay functions.

The reliability of protection schemes can be impacted by CT saturation during faults, resulting in measurement errors or relay malfunctions [1]-[2]. Contemporary numerical relays endeavor to resolve CT saturation concerns by employing stabilization techniques and processing initial saturation-free current measurements. Nevertheless, the operation of low-impedance bus differential schemes can still be impacted by severe CT saturation, particularly under high fault currents. It is imperative to test these relays under extreme saturation conditions to guarantee their rapid, reliable, and secure operation during short circuit faults.

Several studies have examined how CT saturation affects protective systems. Approaches employing ANN have been developed to identify and rectify CT saturation-induced waveform distortions [3]-[4]. These methods adjusted current measurement inaccuracies to ensure protective relay accuracy during transient or fault events. Furthermore, smart sensors using FPGAs technology can detect CT saturation during inrush current circumstances with excellent efficacy, noise immunity, and accurate results across various operating settings. Real-time monitoring of CT magnetic cores was also conducted to detect saturation and residual magnetization and ensure algorithm operability under noise and impulse actions [5]. In power systems, transient compensation of current transformers is essential for handling problems such as quick load-transient responses and CT saturation. Several techniques have been suggested to improve CT performance. These include the use of unscented Kalman filters for quick compensation of CT saturation [6], implementation of a transient output-current regulators for rapid load transient responses, and adoption of transformer-based frameworks with feature compensation and aggregation for Deepfake detection [7]. These methodologies strive to enhance the precision, effectiveness, and dependability of existing transformers by tackling issues such as CT saturation, load transient responses, and counterfeit detection. By using sophisticated methods such as Kalman Filters, output-current regulators, and transformer-based frameworks, the power system may improve the performance and efficiency of current transformers in different applications, guaranteeing dependable operation and safeguarding the system [8]. Generator protection also faces challenges due to the CT saturation, impacting the reliability of relay protection devices. Several techniques have been suggested to tackle the problem of CT saturation. A technique was developed to enhance accuracy and interpretability by combining a FCN for CT saturation detection with a physical model for compensating [9]. Stacked denoising autoencoders, a kind of deep learning technology, showed high accuracy in detecting CT saturation, hence improving the resilience of protection systems [10]. UWLS Dynamic State estimate algorithm is an innovative approach that allows real-time estimate of CT primary current. This algorithm was used to improve the performance of protective relays by boosting their ability to respond quickly and accurately [11]. In addition, recommendations derived from proven CT models were used to assist in selecting suitable CTs for generator protection, considering aspects such as remanence and relay settings [12]. Another method using an UKF was developed to anticipate and rectify the nonlinear components of the waveform, providing superior effectiveness and little intricacy [13]. Furthermore, a new CT design incorporating a virtual air gap and MFS was developed to correct distorted secondary currents and increase the range of measurements. However, this requires the use of high permeability materials to ensure accuracy [14]. Additionally, adaptive error compensation techniques that rely on segmentation and dimensionality reduction have been suggested to enable closed-loop measurement and expand the capabilities of low-voltage CT [15]. Comparative assessments of several mathematical techniques for signal recovery emphasized the stability and sensitivity of these approaches, even in the presence of noise and remanent magnetization [16]. A previous study investigated the use of passive and active compensating methods for broad frequency and range CT to provide precise metering and dependable protection in contemporary power systems. This approach involved avoiding core saturation by using adjustable resistor in conjunction with an auxiliary transformer [17]. The combination of several techniques contributes to the progress of compensating algorithms for CT, improving the dependability and precision of power system protection. Addressing the complex difficulty of compensating for distortion in the secondary current of CT produced by saturation and remanence involves both detecting and correcting these distortions. Saturation often occurs due to elevated fault currents or the existence of an exponentially decaying DC component. This leads to a distorted waveform of the secondary current, which may result in relay protection system failures [18]. In addition, researchers have examined mathematical techniques for retrieving the current signal in saturation mode. The most favorable approaches have shown stability and sensitivity, even in the presence of noise and remanent magnetization [19]. The challenge of PS resulting from stray fluxes has been effectively addressed by the introduction of flux equalizing windings. These windings play a crucial role in ensuring the accuracy of the CT performance and preventing any malfunctions in relays [20]. Analyzing the impact of irregular components on CT transfer characteristics may be done by comparable circuit models. These models aid in comprehending and reducing the negative impacts on relay protection and energy measurement [21]. When there is a loss of information, synthetic current techniques may be used. However, these methods need to be carefully controlled to prevent errors caused by inrush currents and CT saturation [22]. To mitigate the impact of remanence on the precision and dependability of devices such as ground-fault current interrupters, using twin transformers for detecting residual currents is a reliable solution. This approach not only prolongs the lifetime of the device but also ensures that its reaction time remains consistent [23]. Artificial neural networks have been successfully used with conventional techniques to identify CT saturation quickly and reliably. This combination has shown promising outcomes in ensuring the accuracy of secondary current measurements [24]. By using these integrated methods, the negative effects of saturation and remanence are successfully counteracted, hence upholding the dependability and precision of power system protection strategies. The use of wavelet transforms and regression methods to compensate for the secondary current of CT effectively tackles the crucial problem of CT saturation. This saturation may result in the malfunctioning of protective relays and imprecise measurements. Wavelet transforms are highly efficient in differentiating between internal faults and magnetizing inrush currents, even in the presence of CT saturation. This is achieved by examining the DWT characteristics of primary and secondary differential currents and flux measurements [25]. This technique improves the precision of fault classification algorithms, which are often hindered by CT saturation [2]. Alternatively, SVR may be used to correct the distorted secondary current caused by CT saturation. Enhanced utilizing PSO, SVR provides exceptional precision and resilience against noise and abrupt current fluctuations. This makes it a dependable approach for compensating for CT saturation, as stated in reference [26]. In addition, deep learning methods have shown potential in recreating undistorted waveforms from saturated ones, hence improving the precision of secondary current measurements [27]. To enhance the harmonic measuring capabilities of CT and mitigate harmonic distortion, basic signal processing approaches may be used with these techniques. This is essential for effective power quality control [28]. Additionally, hardware techniques such as negative voltage feedback may be used to keep the magnetic flux of CT below saturation levels, guaranteeing dependable performance in different failure scenarios [29]. By integrating these sophisticated methodologies, the overall precision and dependability of CT in power systems may be substantially enhanced, effectively tackling the issues caused by CT saturation and optimizing the functionality of protective relays and measurement systems. Overcurrent protection utilizing signals obtained from saturated measurement CT poses challenges due to the adverse effects of CT saturation on protective schemes [30]. CT saturation can lead to malfunction of protective relays, impacting the accuracy of current measurements and protective actions [31].  Signal generation from Iron-core CT of saturated measurement can prevent maloperation, and they adapted by using algorithms to predict the primary current using distorted secondary current analysis [32]. Meanwhile, an inverse time overcurrent relay, which is prone to fault-induced saturation, is designed for iron-core CT. The algorithm accurately predicts primary currents from distorted secondary current, ensuring reliable operation and reducing mul-operation risks. Testing on an analogue bench under deep saturation confirms its effectiveness in accurate measurement and timely circuit breaker tripping [33]. A method for detecting remanent flux in protection current transformers using fluxgate theory. By analyzing the second harmonic of the induced voltage from a high-frequency source, the remanent flux can be determined through a linear relationship. This approach enables in situ detection, avoiding the need to remove the CT for testing, and is validated through simulations under various conditions. The method is practical and adaptable, though calibration is needed for different transformer models​ [34]. A new technique for reconstructing defect profiles using MFL data from multiple directions. It addresses the limitations of unidirectional MFL detection, where information can be lost due to signal cancellation. The algorithm applies Tikhonov regularization to solve the inverse problem, ensuring more accurate and stable profile reconstruction. The method improves the completeness of the defect opening profile by combining MFL signals without cancellation [35].

TABLE 1. The comparison of highlight different articles

| Ref. | Goal/ Highlight | Data driven | Algorithm | Simulation | Factory test/ Field test | Laboratory test | Real time platform | Real system testing |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| [3] | Real-time detection of CT saturation |  |  |  |  |  |  |  |
| [4] | Improve the accuracy of current measurements by predicting and compensating for errors caused by CT saturation. |  | ANN |  |  |  |  |  |
| [5] | The development of a method to detect and correct the distorted secondary currents of CT caused by saturation |  | ANN |  |  |  |  |  |
| [6] | Transformer protection by proposing a current-compensation-based enhancement for differential relays in non-fault-related disturbances |  | An auxiliary current-compensation method |  |  |  |  |  |
| [7] | To improve the detection of deepfake content using transformer models |  | The method of compensating for the distortions or artifacts. |  |  |  |  |  |
| [8] | Analyzing the fast transient over voltages that occur in CT during the switching operation of disconnectors |  | Methods for analyzing the overvoltage phenomenon with fast transients. |  |  |  |  |  |
| [9] | A hybrid method that combines physical modeling of CT behavior with data-driven techniques |  | Machine learning or statistical analysis |  |  |  |  |  |
| [10] | The rapid detection of CT saturation by utilizing stacked denoising autoencoders (SDAEs) |  | Deep learning and neural network models |  |  |  |  |  |
| [11] | A method for correcting errors caused by CT saturation in merging units (MUs) using dynamic state estimation (DSE) techniques |  | Dynamic state estimation (DSE) techniques |  |  |  |  |  |
| [12] | The key factors that influence CT sizing and practical guidelines |  | The examines of CT application test |  |  |  |  |  |
| [13] | The enhancement of transformer protection by the ratio differential protective relay |  | The optimizing the current compensation algorithm |  |  |  |  |  |
| [14] | A new design for CT that incorporates the concept of a virtual air gap to improve their measurement performance |  | The innovative magnetic circuit design and operational adjustments |  |  |  |  |  |
| [15] | Apply the UKF algorithm processes the CT signals to remove the effects of saturation and distortion |  | The Unscented Kalman Filter (UKF) |  |  |  |  |  |
| [16] | To combines two key techniques: segmentation and dimensionality reduction in proposed algorithm |  | An adaptive error compensation method and dimensionality reduction technique |  |  |  |  |  |

TABLE 1. The comparison of highlight different articles (cont.)

| Ref. | Goal/ Highlight | Data driven | Algorithm | Simulation | Factory test/ Field test | Laboratory test | Real time platform | Real system testing |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| [17] | The comparison of different mathematical compensation methods to restore the original current waveform under CT saturation conditions |  | Fourier-based approaches, Wavelet transform methods, Artificial intelligence and Machine learning techniques and other related |  |  |  |  |  |
| [18] | An adjustable switched resistor demagnetization method to alleviate the issue of CT core saturation and improve the performance of protection systems. |  | The algorithm monitors and control of adjustable switched resistor demagnetization method |  |  |  |  |  |
| [19] | An innovative design approach involving flux equalizing windings to mitigate the effects of partial saturation |  | the separable nonlinear least squares method and morphological filtering |  |  |  |  |  |
| [20] | Improving the performance and accuracy of inductive CT when measuring distorted currents |  | A frequency-domain analysis |  |  |  |  |  |
| [21] | The impact of aperiodic components of current on the risk of CT saturation |  | Mathematical models |  |  |  |  |  |
| [22] | Addressing protection system challenges caused by inrush currents and CT saturation |  | Flux-based or current-based models |  |  |  |  |  |
| [23] | improving the detection accuracy of remanence in more complex magnetic core materials |  | Integrated sensors or signal processing techniques to detect the presence of residual magnetism. |  |  |  |  |  |
| [24] | To correct or restore distorted current waveforms caused by the saturation of CT |  | ANN |  |  |  |  |  |
| [25] | To correct or compensate for the distortions caused by CT saturation |  | PSO and SVR |  |  |  |  |  |
| [26] | A novel technique for distinguishing between transformer internal faults and magnetizing inrush currents |  | Wavelet transform |  |  |  |  |  |
| [27] | Effective method for compensating harmonic distortion in CT |  | Fourier-based harmonic analysis |  |  |  |  |  |
| [28] | Compensate for errors in measurement CT |  | Artificial Neural Network (ANN) |  |  |  |  |  |

TABLE 1. The comparison of highlight different articles (cont.)

| Ref. | Goal/ Highlight | Data driven | Algorithm | Simulation | Factory test/ Field test | Laboratory test | Real time platform | Real system testing |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| [29] | A practical and effective method to reduce or eliminate harmonic distortion in the secondary current of CT |  | Deep learning |  |  |  |  |  |
| [31] | Enhances differential protection schemes by making them sensitive to small faults while compensating for CT saturation |  | Signal reconstruction methods |  |  |  |  |  |
| [32] | A method for enabling reliable overcurrent protection in power systems using saturated CT signals. |  | Fourier Transform or Wavelet Analysis |  |  |  |  |  |
| [33] | Designing an overcurrent relay that works effectively with measurement CT, addressing issues such as saturation and nonlinearity |  | Post-event analysis |  |  |  |  |  |
| [34] | The remanent flux can detect the remanent flux with high accuracy |  | A remanent flux detection method based on the fluxgate theory |  |  |  |  |  |
| [35] | a novel approach to improve the accuracy of reconstructing defect profiles by using MFL data |  | A model-based inversion algorithm |  |  |  |  |  |
| Proposed | Low cost of hardware implements on site |  | SDOFP |  |  |  |  |  |

From previous literature studies, the hardware platform with saturation detector has not been tested in the protective relay function and applied in the power distribution network. The main aim of this study is to design and provide a monitoring platform and test the proposed saturation detector with a low-cost hardware upgrade for load break switch in Ban Khun Pae, Chiang Mai, Thailand.  The main objectives are:

• Studying short circuits in the power distribution system according to IEC 60909, considering short circuit current in both grid-connected and islanding modes using the DIgSILENT program.

• Testing and simulating the transient conditions of current transformers saturation using a current source transformer and the PSCAD program.

• Testing the proposed saturation detector algorithm settings of current transformers using OMICRON 356 in the laboratory under both saturated and unsaturated conditions.

• Installing and testing the proposed hardware upgrade with the algorithm by using the saturation detector and platform to verify the accuracy of the fault detection compared to fault detectors installed on-site.

• Implementing the proposed low-cost hardware upgrade with the algorithm in LBS for Ban Khun Pae, Chiang Mai, Thailand.

This paper is divided into six sections. Section I provides an introduction and review of previous work. Section II provides background theory in research. Section III covers research methodology for simulation experiments. Section IV provides the hardware platform design with results from laboratory testing of the proposed technique. Section V presents the field testing of the hardware platform design at Ban Khun Pae, Chiang Mai, Thailand. Section VI provides conclusions of the presented work.

# 2. Background theory in research

## 2.1 Smart microgrid, Ban Khun Pae village, Chiang Mai, Thailand

The PEA has devised an electric power network development plan aligned with the economic and social development plan. The electric power network is being developed to support distributed generators and renewable energy resources, as well as efficient energy management technology in the future. The PEA has identified the development of a microgrid project in Khun Pae Village, Chiang Mai, Thailand, as shown in Fig.  1, as one of the developments needed to transform electric power networks into the electric utility of the future with the aim of 100% electrification for PEA's area of responsibility.

FIGURE 1. Single line diagram of a microgrid in Ban Khun Pae village.

Figure 1 shows diagram of a microgrid in Ban Khun Pae village with the maximum main load demand is approximately 69.85 kW.  Two modes of load demand have been assessed, which consisted of normal and water saving modes. The monthly averages for electricity generation in one year for this research were discussed by [36]. The IEEE 2030.7 – IEEE standard provides the specification for microgrid controllers. Microgrid control and protection system is beyond the scope of this research. This research focused on detecting faults in the feed lines of the distribution system at various zones, namely Zone 1, Zone 2, Zone 3, and Zone 4. The budget for the microgrid's control and protection system budget does not include the cost of upgrading the existing FRTU with hardware algorithm at the LBS.

## 2.2 Existing Load Break Switch (LBS) and Feeder Remote Terminal Unit (FRTU)

The FRTU is designed to connect to the TDMS command center. The LBS is used to connect and open circuits in the distribution line with a maximum load current of 630 A. The LBS is operated by remote commands from the dispatch center through a communication media. The typical layout of the LBS and FRTU configuration consists of PLC-based LBS controller, digital I/O, analog input and communication module, as shown in Fig. 2 (a). The typical installation of the LBS and FRTU is shown in Fig. 2 (b).  The LBS and FRTU typically use PLC function with metering CTs, with an installed base of around 95 % for distribution system.

(a) Typical layout of the LBS and FRTU configuration

(b) Typical installation of the LBS and FRTU

FIGURE 2. The existing LBS and FRTU at Ban Khun Pae.

The existing FRTU at Ban Khun Pae, Chiang Mai, Thailand consists of PLC-based LBS controller, digital I/O, analog input, IEDs and communication module, as shown in Fig. 3. An additional IEDs relay is used for the detection of fault conditions and their locations. The IEDs relay analyzes current and voltage signal and derives fault conditions based on the output obtained by analyzing the signals. Later, IEDs relays were further developed and deployed for the new FRTU with an installed base of around 5 % for distribution system.

FIGURE 3. Existing layout of the LBS and FRTU configuration with additional IEDs relay

The relay settings were configured to a single value, corresponding to grid-connected mode as presented by TABLE 2.

TABLE 2. Parameter setting of 50/51 overcurrent relay

| Setting Title | Value | Unit |
| --- | --- | --- |
| 50/51 P1.I_setting | 50 | A |
| 50/51 P1.t_setting | 0.1 | s |
| 50/51 P2.I_setting | 15 | A |
| 50/51 P2.t_setting | 0.1 | s |
| 50/51G PG.I_setting | 50 | A |
| 50/51G PG.t_setting | 0.1 | s |

## 2.3 Saturation detector

The main aim of saturation detector is to accurately identify the fault location and service restoration for distribution feeders. This paper implements an algorithm for a saturation detector designed for overcurrent protection relays. The algorithm consists of a signal conditioner for scaling and eliminating interference signals. The saturation detector algorithm was designed to detect the healthy parts within the saturated current signals. The unsaturated parts were then used in relay algorithms to enhance speed and accuracy. The architectural design of the online fault detection system involves connecting through sending information over the internet. Upon fault detection, the saturation detector transmits the measured fault signal to the server using HTTPS. The server then calculates the results and stores the fault signal in the HMI. Users can access data showing all events and fault values using FRTU.

A saturation detection algorithm selects only signals of good quality without saturation (non-saturation), while disregarding the distorted signal with saturation (saturation). The algorithm determines the magnitude of the signal current and angle at any time using the saturation detector, as shown in Fig. 4. This method converges to the correct size faster than the Fourier transform methods such as the FCDFT and HCDFT. Basically, the saturation detector consists of two filters. The first filter ∅(𝑘) is a partial sinusoidal signal, and the second filter ∅𝑐(𝑘) is a partial signal of the cosine signal ∅(𝑘) and ∅𝑐(𝑘), and both must be perpendicular to each other. If the data window has a sampling period Δt and length L, which is an odd integer, ∅s(𝑘) and ∅c(𝑘) can be constructed as shown in equations (1) and (2), respectively.

∅sk=sinω0k∆tγs                                                                       (1)

∅ck=  cosω0k∆t-sin0.5*ω0L∆t0.5*ω0L∆tγc                                             (2)

When

k ∈ L-12-L-1,L-12-L-2, …,L-12-L-L

where

γS and γC could be calculated using equations (3) and (4), respectively. Both values represent the energy values of the impulse response of the sinusoidal and cosine filters at the fundamental frequency, respectively.

γs=         k=1-L2L-12sin2ω0k∆t                                                        (3)

γc=        k=1-L2L-12cosω0k∆t-sin0.5ω0L∆t0.5ω0L∆t×cosω0k∆t             (4)

The magnitude and angle of the current signal can be calculated by passing the current signal i(n) through a convolution process with the filters ∅s(𝑘) and ∅𝑐(𝑘), as shown in equations (5) and (6), respectively. The results obtained from both equations represent the real magnitude anand the imaginary magnitude bn of the i(n) signal. Therefore, the signal current I1n can be calculated as shown in equation (7).

an=in*∅sk                                                                               (5)

bn=in*∅ck                                                                                     (6)

I1n=a2n+b2n                                                                         (7)

FIGURE 4. Chart of the signal quality indication

The saturation detector passes In to the ∆In rate of change section, using the calculation in equation (8).

∆In=In-In-1                                                                       (8)

Once the ∆In value is obtained, it is passed through a moving average low pass filtering process to smooth the signal. Then, the absolute value of the rate of change in magnitude, or ∆In  is determined. If the current signal is of good quality, the value∆In will be very low. To check if ∆In is low, the value is compared with the Marginmag value. If ∆In is lower than the Marginmag, the Magnitude Fail (Mag. fail) indicator remains inactive. Conversely, if ∆In is higher than the Marginmag, the Mag. fail indicator signal value becomes active, indicating that the signal is of poor quality. To check whether the angle-of-change rate of the signal is 360 degrees per period, the value θn, sent by the saturation detector, is passed to the rate of change  ∆θn section using the calculation in equation (9).

∆θn=θn-θn-1                                                                    (9)

Once ∆θn is obtained, the algorithm checks if ∆θn is negative. If it is negative, then 360 degrees is added. After that, the rate of change of angle is checked to determine if it is 360 degrees per period. If the absolute value of the difference between ∆θn and 360/N is less than the Margin θ value, the ∆θ Fail indicator value remains inactive. Conversely, if the ∆θn value differs from the 360/N value by more than the Margin θ value, the ∆θ fail indicator value becomes active, indicating that the signal is of poor quality. If both the Magnitude Fail (Mag. fail) and ∆θ Fail indicators are inactive, the Saturation Flag indicator signal becomes active. This signal indicates whether the signal at that time is of good quality.  An active Saturation Flag indicates good signal quality, which is then used to adjust the current signal to maintain good quality [37].

## 2.4 Magnitude evaluation

When the “non-saturation” flag is set, the current magnitude correctly represents the magnitude of the primary current signal. However, when the flag is reset, the current magnitude becomes erroneous. The concept of the magnitude evaluator is to utilize the current magnitude only when the flag is set. The most recent magnitude value determined when the flag is set is retained when the flag is reset. When the flag is set again, a new magnitude value is calculated and updated for every sample. Therefore, the magnitude evaluator continuously produces a discrete estimation of the primary current magnitude in real time for every new sample.

FIGURE 5. The results of the magnitude evaluator

Figure 5 shows the flag used to detect when the signal is not saturated (non-saturation flag) and the calculated peak “primary” current magnitude. Although the current is severely distorted by the effect of CT saturation, the saturation detector is able to detect non-saturated periods. These periods occur when the non-saturation flag (represented with a thin solid line) is set to high. The dotted line represents the calculated current magnitude of the fundamental component of the primary current, i.e. the magnitude of the signal if the CT had been an ideal (non-saturated) 1:1 transformer and after the removal of the exponential offset. The calculated magnitude fluctuates significantly during the saturated periods but remains reasonably constant during the non-saturated periods. As the magnitude evaluator works, the current magnitude calculated during the non-saturated and saturated periods is converted into a magnitude result that is only updated within the non-saturated periods. During each saturated period, the magnitude evaluator holds the last magnitude value calculated during the previous non-saturated period. Hence the current magnitude result (represented with a thick solid line) shows the peak magnitude of the fundamental component of the “primary” fault current [38].

# 3. Research Methodology for Simulation Experiments

## 3.1 Analysis of the short circuit using DIgSILENT

The analysis of the short circuit in the power distribution system of the Ban Khun Pae microgrid project was conducted using the DIgSILENT program, as shown in Fig. 6.

FIGURE 6. LBS S1, S2, S3 and S4 at Ban Khun Pae microgrid project

The objective was to determine the short-circuit current according to IEC 60909 at the LBS S1, S2, S3 and S4, in both grid-connected and islanding modes. The results are shown in TABLE 3 and TABLE 4 [39].

TABLE 3. Short circuit current in (Isc)-grid connected mode

| Fault Type (IEC60909) | Fault Location(kA) |  |  |  |
| --- | --- | --- | --- | --- |
|  | S1 | S2 | S3 | S4 |
| Three Phase | 1.025 | 1.120 | 0.996 | 0.837 |
| Single Line to Ground | 0.125 | 0.155 | 0.156 | 0.151 |
| Line to Line | 0.891 | 0.957 | 0.849 | 0.715 |
| Double Line to Ground | 1.025 | 1.197 | 1.095 | 0.894 |

TABLE 4. Short circuit current in (Isc)- island mode

| Fault Type (IEC60909) | Fault Location(kA) |  |  |  |
| --- | --- | --- | --- | --- |
|  | S1 | S2 | S3 | S4 |
| Three Phase | 0.127 | 0.127 | 0.129 | 0.127 |
| Single Line to Ground | 0.125 | 0.155 | 0.156 | 0.151 |
| Line to Line | 0.095 | 0.095 | 0.096 | 0.095 |
| Double Line to Ground | 0.146 | 0.190 | 0.190 | 0.180 |

The IEC 60909 can be applied for calculating short-circuit currents in low-voltage three-phase AC systems, and in high-voltage three-phase AC systems, operating at a nominal frequency of 50 Hz. The author has explained the suggestions. This research mainly focused on detecting and locating fault locations in a LBS. If a permanent fault is detected through the DNP3 communication system to the Transmission and Distribution Management System (TDMS) command center, PEA will then dispatch personnel to the fault location. This reduces the time required to find the location of the fault and restores the electrical system to normal more quickly. In the event of a single line to ground fault through LBS S1 or LBS S2 or LBS S3 or LBS S4 at Khun Pae, if the fault is temporary, the Microgrid will remain connected to the grid in grid-connected mode.  However, in the case of a permanent fault causing the 22 kV or 115 kV transmission line linking from the HOD substation to go offline, the microgrid will operate in islanded mode, disconnecting from the grid.

## 3.2 Study and testing of the transients using a current source transformer

The study and testing of the transients using a supply current source transformer aimed to detect the saturation state of the current transformer by supplying the primary current at different current levels. An image of the test circuit at the manufacturer’s laboratory at Precise Electric manufacturing is shown in Fig. 7. The test showed that the secondary current began to deviate from the sinusoidal waveform when the primary current was increased from 60 Arms, with the saturation condition increasing when a 90 Arms primary current was supplied.

FIGURE 7. Circuit testing of the CT using the current source transformer

For the CT saturation studies, the test was divided into 13 assessments, which took into account the current size of the primary and burden dimensions, as shown in TABLE 5.

TABLE 5. Testing CT 10/1, 5 VA, Class 0.5

| Technical Data for the Current Transformer at the LBS S1 |  |
| --- | --- |
| Highest System Voltage (kV) | 24 |
| Rated Frequency (Hz) | 50 |
| Rated Primary Current (A) | 10 |
| Rated Secondary Current (A) | 1 |
| Output Burden (VA) | 5 |
| Accuracy Class | 0.5 |
| Short Time Current Rating (kA, 1 sec) | 1 |
| Dynamic Current Rating (kA peak) | 2.5 |
| Rated Continuous Thermal Current (%) | 120 |
| Insulation Class | A |
| Maximum Temperature Rise of Winding (K) | 60 |
| Maximum Ambient Temperature (℃) | 40 |
| Basic Impulse Level Impulse Withstand Voltage (kV peak0) | 125 |
| Power Frequency Withstand Voltage |  |
| Primary Winding (kVrms) | 50 |
| Secondary Winding (kVrms) | 3 |

TABLE 6 shows the rated primary current, rated secondary current, and output burden for the CTs metering parameters at the LBS S1 as proposed.

TABLE 6. Current transformer parameters

| Test Case No. | Primary Current (A) | Burden @ Power Factor = 0.9 |  |
| --- | --- | --- | --- |
|  |  | Resistance (ohms) | Inductance (mH) |
| 1 | 5 | 0 | 0 |
| 2 | 8 | 0 | 0 |
| 3 | 10 | 0 | 0 |
| 4 | 12 | 2.97 | 4.58 |
| 5 | 18 | 2.97 | 4.58 |
| 6 | 20 | 2.97 | 4.58 |
| 7 | 25 | 2.97 | 4.58 |
| 8 | 30 | 2.97 | 4.58 |
| 9 | 40 | 2.97 | 4.58 |
| 10 | 60 | 5.94 | 9.1 |
| 11 | 80 | 5.94 | 9.1 |
| 12 | 90 | 5.94 | 9.1 |
| 13 | 100 | 2.97 | 4.58 |

The analysis results of the technical data tested using the current source transformer for test case no. 12 are shown in Fig. 8.

FIGURE 8. Primary current (Ip) and secondary current (Is) using the current source transformer testing for test case no.12 @ 90 A with the burden of 6.6 ohms

## 3.3 Model study and transient test using PSCAD

The model study and transient testing using the PSCAD program aimed to detect the saturation state of the current transformer by modeling, as shown in Fig. 9. The primary current was supplied at different current levels to compare the effectiveness of the current source transformers.

FIGURE 9. Schematic representation of the CT using PSCAD

The analysis results of the technical data tested using simulation software PSCAD for case no.12 with an applied primary current of 90 Arms (127.28 Apeak) are shown in Fig. 10.

FIGURE 10. Primary current (Ip) and secondary current (Is) for test case no.12 @ 90 A with the burden of 6.6 ohms

The results showed that simulation software and experimental testing using a current source transformer yielded slightly different secondary current values in all case studies.

# 4. Hardware Platform design

## 4.1 Modification of FRTU with hardware algorithm at the Ban Khun Pae project, Chiang Mai, Thailand

The FRTU was modified by integrating a hardware algorithm designed to connect to the dispatching center of PEA. The FRTU consists of PLC-based LBS controller, digital I/O, analog input, IEDs, communication module and the additional hardware algorithm. Fig. 11. Shows: (a) typical FRTU and (b) FRTU with hardware algorithm.  The additional hardware algorithm is designed to detect fault conditions similar to the functionality of IEDs relay. Additionally, it includes the ability to detect non-saturation and saturation conditions.

(a) Typical FRTU

(b) FRTU with hardware algorithm

FIGURE 11. The layout comparison of the LBS and FRTU configuration

## 4.2 Hardware platform design using CPU MSP430 processing unit

The hardware platform is designed to attenuate the signal entering the 24-bit ADC for sampling algorithms and reporting the status of fault signals. Input signals are scaled to a suitable size and high pass filtered to remove noise. The hardware platform consists of an ADC converter, Diff Amp, Voltage Divider, Signal Conditioner and CPU MSP430 Processing Unit, as shown in Fig. 12.

FIGURE 12. The hardware platform design using CPU MSP430 processing Unit

## 4.3 Hardware platform working process

The working process of the hardware platform consists of 3 sets of saturation detectors, each detecting a separate phase, corresponding to phases A, B and C, as shown in Fig. 13. When the result signal is obtained, it connects to the database system via the WIFI signal of the 4G Router. The working process of each phase operates similarly. Starting with the signal conditioning process, the current signal is received from the CTs. Subsequently, the signal is adjusted and converted into a voltage form.

The frequency is filtered within the range of interest and the amplitude adjusted to fit the scale of the analog-to-digital converter. Then the analog-to-digital converter converts the current signal to digital form, sampling 100 current points per cycle or 5 kHz. The API for algorithm is defined by algorithm detecting the magnitude of the current signal and its angle at any time using the Short Data Window Orthogonal Filter Pair (SDOFP) method [38]. The saturation detector algorithm separates the current and phase angle values, detecting changes in both to identify saturation and to compensate for current values and phase angles. Once the saturation is detected, the result is sent to the database. After that, it detects overcurrent conditions. Upon overcurrent detection, it records the waveform for 500 points and sends the results to the database for display through the webserver HMI. The communication data is responsible for receiving data at each process and sending it to the database, including saturation, fault occurrences and fault waveforms.

FIGURE 13. Chart of hardware platform working process

## 4.4 Hardware algorithm process

The hardware algorithm process is used for detecting distortion in the current signal, as shown in Fig. 14. There are two important variables: magnitude and angle θ. In other words, a good signal should exhibit normal changes, including sudden changes in magnitude that do not exceed the specified value (saturation value setting). This normal value is obtained from simulations. The change in the angle value ∆θ, according to the degree of the sinusoidal waveform, must also be equal to 0. This paper has designed a value setting (Error ∆θ value setting) for use in the study. As seen in Fig. 14, the current value with parameters In and ∆n is compared with the previous values of In-1 and θn-1  to find the difference. The parameters ∆I and ∆θ represent the difference between current and angle. Then, the program uses these differences to classify the signal as either good (non-saturation) or distorted (saturation). A good signal must have ∆I and ∆θ outputs that do not exceed the specified limit. If the difference is higher than the specified limit, the signal is classified as saturation, which is then adjusted or compensated (compensation) before being analyzed for fault detection.

FIGURE 14. Saturation detector algorithm process

## 4.5 Algorithm design of the saturation detector

The algorithm design of the saturation detector used the function of the overcurrent protection relay, as shown in Fig. 15. It consists of a signal conditioner, which scales, and eliminates interference signals. It also includes the MCU, which is optimized for efficiency, as the main part that calculates and detects the saturation. The waveforms are recorded, and the communication is managed between the commutation controller board and the database server. The test was performed using the Texas MSP430 series using 15 saturation detector data points to process the digital correlations with a sampling rate of 4,000 Hz. The cost of upgrading the existing FRTU along with building the saturation detector was only $200 per set. The FRTU upgrade also enabled efficient fault detection in the distribution system, providing reliability comparable to newer FRTUs with higher costs and relay functions.

FIGURE 15. System design for the saturation detector

For digital data to be used in calculations, accurate voltage and current measurements are important. Therefore, conditioning of the analog signal is required for accuracy before processing. The main principle of good signal measurement is ensuring the signal is of the appropriate size. This includes limiting the range of voltage and current to the frequency range under consideration and making it suitable for use with ADC. Therefore, the voltage and current are scaled down to a size suitable for the device and low pass filtered to remove noise or signals outside the range of interest. The digital signal used for processing is created by converting the analog signal in a repeated format and at intervals according to the specified signal sampling frequency or sampling rate. During the signal sampling period, the CPU processes the data according to the designed algorithm, such as saturation and fault detection. Therefore, CPU processing speed is very important for digital processing. All tasks must be calculated and processed before new signals are sampled. In this research, the main equipment was separated into 3 levels:

Level    1 : Digital signal processing set

Level    2 : TCP/IP communication set via wireless technology (WIFI)

Level    3 :  Industrial grade 4G for communication set

## 4.6 Laboratory testing of the saturation detector algorithm

The circuit of the saturation detector algorithm was tested in the laboratory, as shown in Fig. 16. The primary objective was to test the algorithm in the saturation detector integrated into the FRTU using Omicron 356 to detect faults and determine the fault location.

FIGURE 16. Circuit testing of the saturation detector integrated into the FRTU using Omicron 356

In the case of use under normal conditions with a rated current of 90 amps, the test results showed that the secondary current signal waveform at Phase A contained both unsaturated and saturated signals. The positive signal was in the range of 0-90 degrees and 180-270 degrees, respectively. The magnitude of the secondary current exceeded the set value, resulting in tripping. The fault detector showed a value of 1, as shown in Fig. 17 (Phase A) and Fig. 18 (Phases A, B, and C).

FIGURE 17. Test results of the saturation detector for test case no. 12 @ 90 A

FIGURE 18. Test results of the saturation detector for test case no.12 @ 90 A (Phase A, Phase B and Phase C)

The saturation detector circuit was tested using Omicron 356 in the laboratory to assess the algorithm. It was found that faults could be accurately detected.

## 4.7 THE SATURATION DECTOR ALGORITHM PERFORMANCE TEST

The performance testing of the algorithm on the saturation detectors was conducted for each type of fault current using the function of an overcurrent protection relay to detect the unsaturated current, saturation current, overload current, and the fault current. The algorithm performance test results showed that all types of faults were detected, as summarized in TABLE 7.

TABLE 7. Performance of the saturation detector algorithm

| Type of Fault | Non-Saturation Detection | Saturation Detection | Overload Detection | Fault Detection |
| --- | --- | --- | --- | --- |
| Phase A to Ground | Detected | Detected | Detected | Detected |
| Phase B to Ground | Detected | Detected | Detected | Detected |
| Phase C to Ground | Detected | Detected | Detected | Detected |
| Phase AB | Detected | Detected | Detected | Detected |
| Phase BC | Detected | Detected | Detected | Detected |
| Phase CA | Detected | Detected | Detected | Detected |
| Phase AB to Ground | Detected | Detected | Detected | Detected |
| Phase BC to Ground | Detected | Detected | Detected | Detected |
| Phase CA to Ground | Detected | Detected | Detected | Detected |
| Phase ABC | Detected | Detected | Detected | Detected |
| Phase ABC to Ground | Detected | Detected | Detected | Detected |

## 5. Field testing of hardware platform

## 5.1 Online fault detection of hardware platform

This test focused on the online fault detection system integrated into the saturation detector. The accuracy of its fault detection was verified by comparing it to the fault detector installed at the smart microgrid project in Ban Khun Pae, Chiang Mai, Thailand. The architectural design of the online fault detection system involves connecting through sending information over the internet. When a fault occurred in the power distribution system, the integrated fault detection system within the saturation detector at the LBS S1, S2, S3 and S4 positions detected and transmitted the measured fault signal to the server. The server calculated the results and stored them in a database for the Human Machine Interface (HMI). Users could access data showing the events and fault values using the FRTU, including the current record, fault values and a map service indicating the fault location. An application program was used to display the software interface for processing the information received. Additionally, web services were accessible through a web browser, and the Application Programming Interface (API) transmitted data between the server and the FRTU, and the server to the HMI, as shown in Fig. 19.

The Intelligent Wireless Observing System (IWOS) installed on 22 kV distribution lines or main feeders at Ban Khun Pae, Chiang Mai, Thailand, was field proven by line sensor installations in 2022. Since then, it has accumulated waveform data online events and detected faults, including ground faults and short circuit faults. The system helps PEA to detect and locate faults, reduce power outage, and shift from reactive to preventive maintenance practices. The IEDs relay controller PCS 9721C serves as the feeder remote terminal unit (RTU). It monitors all distribution line or substation equipment and acquires data from all incoming and outgoing feeders on a real-time basis. It captures status signals of devices and conducts automatic data logging to provide distribution line or substation-level control. When the LBS online fault detection system detected a fault, an event of that fault was displayed at the detected FRTU location, as shown in Fig. 20. In this research study, a low-cost hardware upgrade for the LBS was designed and installed in a conventional FRTU, and integrated for testing the LBS S1, S2, S3 and S4. Its fault detection accuracy was compared to that of IEDs relay and IWOS fault detector, which were previously tested and are used at the smart microgrid project in Ban Khun Pae, Chiang Mai, Thailand.

FIGURE 19. The monitoring system architecture of the saturation detector

FIGURE 20. PEA 22 kV distribution line with FRTU at Ban Khun Pae

The transmission system for the online fault detection of the LBS was installed in the FRTU at locations S1, S2, S3 and S4 at the smart microgrid project in Ban Khun Pae, Chiang Mai, Thailand, as shown in Fig. 21. Each FRTU transmitted the fault value of the current, which was then saved to the cloud server via the solution provider's 4G Internet for domestic services. The cloud server processed the data and stored it in the database. Users could access the data through a web browser on mobile phones or laptops, as shown in Fig. 22.

FIGURE 21. FRTU locations at LBS S1, S2, S3 and S4 at Ban Khun Pae

FIGURE 22. The data transmission system for the saturation detector

## 5.2 Field testing of hardware platform on the real system testing

The hardware platform with algorithm were installed in the FRTU of the LBS at locations S1, S2, S3 and S4 at the smart microgrid project at Ban Khun Pae, Chiang Mai, Thailand, as shown in Fig. 23 and Fig. 24, respectively.

FIGURE 23. On-site saturation detector installation at Ban Khun Pae, Chiang Mai, Thailand

FIGURE 24. On-site saturation detector installation at FRTU LBS S1

The test results showed that the saturation detector could detect faults using the function of an overcurrent protection relay. The measured values were examined and compared with those of the fault detectors installed at the smart microgrid project in Ban Khun Pae, Chiang Mai, Thailand, as follows:

- The IEDs relay Controller-PCS 9721C.

- The IWOS with a concentrator that receives the transient zero sequence current and electric field signals, synthesizing all three phases to detect faults and identify ground fault locations using overhead line sensors.

Comparisons of the applications showed that all three types of fault detectors were able to accurately detect faults and record fault current events on the same day and time, as shown in TABLE 8.

TABLE 8. Results of event recorder at FRTU LBS S1

| Item | DMY-Time | Device ID | FRTU |
| --- | --- | --- | --- |
| 1 | 29/10/2021 12:55:13 | HOA07-03 | S1 |
| 2 | 29/10/2021 12:59:40 | HOA07-03 | S1 |
| 3 | 30/10/2021 03:23:53 | HOA07-03 | S1 |
| 4 | 02/11/2021 19:25:38 | HOA07-03 | S1 |
| 5 | 02/11/2021 22:50:35 | HOA07-03 | S1 |
| 6 | 02/11/2021 22:59:41 | HOA07-03 | S1 |
| 7 | 21/01/2022 13:33:00 | HOA07-03 (Original Name: HOA07-03) | S1 |

A total of seven fault events were logged on the FRTU Device ID No. HOA07-03, located at the LBS position S1. The waveform recorded a fault event at Phase C on January 21, 2021, as shown in Fig. 25 and Fig. 26, and recorded fault events on other days, as shown in Fig. 27.

The most common type of fault detected in the system was the single line to ground fault. The other locations, S2, S3 and S4, had very small fault currents because they were installed at the distribution endpoint and had minimum load. The current value was lower than the set value. The number of faults occurring at these locations was infrequent compared to location S1, so the saturation detector did not record a fault event at those points.

FIGURE 25. Event recording at FRTU S1 using IWOS

FIGURE 26. Event recording at FRTU S1 using the saturation detector.

FIGURE 27. Event recording at FRTU S1 using the saturation detector on other days

# 6. Conclusion

This paper plays an important role in improving the reliability of distribution feeders. The main objective of the research was to monitor and test the proposed hardware upgrade with algorithm at Ban Khun Pae, Chiang Mai, Thailand.  The research was successfully conducted, and the key contributions and summary details are as follows:

• This paper presented the short circuit study of Khun Pae Village conducted using the DIgSILENT program in both grid-connected and islanding modes.

• Transient conditions were studied and tested using a current source transformer. Simulation studies and transient testing were carried out using the PSCAD program. The results showed that simulation software and experimental testing using a current source transformer yielded slightly different secondary current values in all case studies.

• The saturation detector test using OMICRON 356 in the laboratory under saturated and unsaturated conditions indicated that faults could be accurately detected. Additionally, the saturation detector algorithm performance test showed that all types of faults were detected.

• The monitoring platform for the online fault detection test results of the saturation detector at the smart microgrid project in Ban Khun Pae, Chiang Mai, Thailand, were presented. Comparisons of the applications showed that all three types of fault detectors, including (1) the IEDs relay controller-PCS 9721C, (2) IWOS, and (3) Saturation detectors were able to accurately detect faults and record the fault current events on the same day and time.

• The implementation of the low-cost hardware upgrade with the algorithm for the LBS was successfully carried out at Ban Khun Pae, Chiang Mai, Thailand as proposed.

Suggestion of future work:

The following are the suggestions for future work based on the experience and the knowledge acquired during the project:

• Use the function of directional overcurrent relay or fault locator within the distribution system.

• Conduct a cost-effectiveness analysis of upgrading existing FRTUs with saturation detectors against installing new FRTUs with relay functions.

Additionally, the FRTUs installed in the distribution system in Thailand are divided into two main groups: Group 1: FRTUs that were originally installed (existing) and use metering current transformers for over 95 % of their systems. These FRTUs are equipped with control and protection relays, with only the overcurrent protection relays and DNP 3 communication system. Conversely, Group 2 FRTUs are deployed in accordance with new technical requirements, with approximately 5 % of the systems having been updated. These FRTUs include additional functions such as directional overcurrent protection relays. Detailed features, including sensitive earth fault detection, broken conductor detection, fault recording, DNP 3 communication system, which comply with IEC 61850, are given in TABLE 9.

TABLE 9. Feeder fault current detection in distribution systems in Thailand

| Feeder Fault Current Protection | Upgraded Existing FRTUs With Hardware Algorithm | New FRTUs with Relay Functions |
| --- | --- | --- |
| Installed base | 95 % | 5 % |
| Fault detection features associated with relays | PLC Based | - Overcurrent (ANSI50/51, 50G/51G) - Sensitive earth fault (ANSI 50SEF) - Directional relay (ANSI 67) - Broken conductor (ANSI 46BC or ANSI 47BC) - Negative sequence voltage (ANSI 47) |
| Communication modules | HTTPS | IEC 61850 or DNP3 |
| Fault events and fault clearance events |  |  |
| HMI Application | None | SCADA Dispatch Control Center (TDMS) |
| Estimated price for upgrading fault current detection function | 200 USD (Approx.) | 2,000 USD (Approx.) |

This research presents the design and testing of a low-cost hardware platform with an estimated price of around 200 USD per unit, for upgrading load break switches for use in intelligent distribution systems. The saturation detector was designed, installed tested, and has been in operation within PEA's system for more than 5 years. The saturation detector allows for algorithm upgrades for fault detection.

REFERENCES

[1]	Ishwarjot Anand, "RTDS Based Testing of Bus Differential Protective Relay Performance in Presence of CT Saturation," Toronto Metropolitan University, 2020.

[2]	Shantilal J Babaria, Dharmesh D Patel, Nilesh G Chothani, Pratap K Chaini, Rajesh M Patel, and Sanjay R Joshi, "Influence of system parameters on current transformer saturation in power system," in 2022 IEEE 2nd international conference on sustainable energy and future electric transportation (SeFeT), 2022: IEEE, pp. 1-6.

[3]	G de J Martínez-Figueroa, Felipe Córcoles-López, and Santiago Bogarra, "FPGA-Based Smart Sensor to Detect Current Transformer Saturation during Inrush Current Measurement," Sensors, vol. 23, no. 2, p. 744, 2023.

[4]	Erastus Mwongela Musyoka and Choong-koo Chang, "ANN based model for current transformers’ saturation error compensation in medium voltage switchgears," Journal of Electrical Engineering & Technology, vol. 17, no. 4, pp. 2171-2179, 2022.

[5]	Luana Barcelos Severo, Eduardo Machado dos Santos, Chrystian Dalla Lana da Silva, Eduardo Davila Kilian, Fábio Kaspary Schons, and Fabiano Aguiar de Oliveira, "A Proposal for Detection and Correction of Current Transformer Distorted Secondary Currents Due to Saturation Using Artificial Neural Networks," in 2022 IEEE PES Generation, Transmission and Distribution Conference and Exposition–Latin America (IEEE PES GTD Latin America), 2022: IEEE, pp. 1-6.

[6]	Amir Ameli, Mohsen Ghafouri, Hatem H Zeineldin, Magdy MA Salama, and Ehab F El-Saadany, "Accurate fault diagnosis in transformers using an auxiliary current-compensation-based framework for differential relays," IEEE Transactions on Instrumentation and Measurement, vol. 70, pp. 1-14, 2021.

[7]	Zichang Tan, Zhichao Yang, Changtao Miao, and Guodong Guo, "Transformer-based feature compensation and aggregation for deepfake detection," IEEE Signal Processing Letters, vol. 29, pp. 2183-2187, 2022.

[8]	Filipe R Gadotti, Sérgio HL Cabral, and Felipe M Schuartz, "Fast transient overvoltage analysis in current transformers due to disconnector switching operation," in 2022 7th International Advanced Research Workshop on Transformers (ARWtr), 2022: IEEE, pp. 58-63.

[9]	Songhao Yang, Yubo Zhang, Zhiguo Hao, Zexuan Lin, and Baohui Zhang, "CT saturation detection and compensation: A hybrid physical model-and data-driven method," IEEE Transactions on Power Delivery, vol. 37, no. 5, pp. 3928-3938, 2022.

[10]	 Sopheap Key, Chang-Sung Ko, Kwang-Jae Song, and Soon-Ryul Nam, "Fast detection of current transformer saturation using stacked denoising autoencoders," Energies, vol. 16, no. 3, p. 1528, 2023.

[11]	 PE Emeka Obikwelu and AP Sakis Meliopoulos, "CT saturation error correction within merging units using dynamic state estimation," in 2020 IEEE 3rd International Conference on Renewable Energy and Power Engineering (REPE), 2020: IEEE, pp. 45-50.

[12]	 Ritwik Chowdhury, Dale Finney, Normann Fischer, and Douglas Taylor, "CT sizing for generator and transformer protective relays," in 15th International Conference on Developments in Power System Protection (DPSP 2020), 2020: IET, pp. 1-6.

[13] Ji, Hyun, Cha., Kwan-Ho, Chun., Jin-Yeub, Park. "Analysis of Current Compensation Algorithm of Ratio Differential Protective Relay for Transformer and Development of Fault Type Identification Logic." The Transactions of the Korean Institute of Electrical Engineers, undefined (2022). doi: 10.5370/kiee.2022.71.6.826

[14]	 Yuwen Wu, Cuihua Tian, Zhexuan Zhang, Baichao Chen, Shaojie Liu, and Yaojun Chen, "A novel current transformer based on virtual air gap and its basic measuring characteristics," IEEE Transactions on Power Delivery, vol. 38, no. 1, pp. 13-25, 2022.

[15]	 Anju Thomas and V Vinod, "Accurate compensation of heavily saturated and distorted Current Transformer output using Unscented Kalman Filter Algorithm," in 2022 IEEE Global Conference on Computing, Power and Communication Technologies (GlobConPT), 2022: IEEE, pp. 1-6.

[16] 	Minrui Xu, Shufeng Lu, Feng Ji, and Gang Chen, "An adaptive error compensation method for wide-range current transformers based on segmentation and dimensionality reduction," in Third International Conference on Computer Science and Communication Technology (ICCSCT 2022), 2022, vol. 12506: SPIE, pp. 321-326.

[17] Ismoil Odinaev et al., "Comparison of Mathematical Methods for Compensating a Current Signal under Current Transformers Saturation Conditions," Sensors, vol. 21, no. 21, p. 7273, 2021.

[18]	 Saeed Sanati and Yousef Alinejad-Beromi, "Avoid current transformer saturation using adjustable switched resistor demagnetization method," IEEE Transactions on Power Delivery, vol. 36, no. 1, pp. 92-101, 2020.

[19] 	Abbas Torkamani, Mahdi Davarpanah, and Majid Sanaye-Pasand, "Resolving current transformer partial saturation problem: An analytical approach to design the flux equalizing winding," IEEE Transactions on Power Delivery, vol. 37, no. 5, pp. 4145-4153, 2022.

[20]	 Michal Kaczmarek and Ernest Stano, "New Approach to Evaluate the Transformation Accuracy of Inductive CTs for Distorted Current," Energies, vol. 16, no. 7, p. 3026, 2023.

[21]	 Zhang Guoxin, Wang Ganlin, Liu Hongshun, Yu Dayang, Wang Qilin, and Chen Long, "Risk analysis of CT saturation caused by aperiodic components," in 2022 IEEE International Conference on Electrical Engineering, Big Data and Algorithms (EEBDA), 2022: IEEE, pp. 01-06.

[22]	Wei Liu, Zhile Xu, Zengchao Wang, Yuxue Wang, Yiquan Li, and Minghao Wen, "Missing Information Protection Considering Inrush Current and CT Saturation," in 2022 2nd International Conference on Electrical Engineering and Mechatronics Technology (ICEEMT), 2022: IEEE, pp. 115-120.

[23] Jayson Loreto, Olga Joy L Gerasta, and Aileen C Gumera, "Residual Current Circuit Implemented in Complementary Metal Oxide Semiconductor for Remanence Correction," in 2020 IEEE 12th International Conference on Humanoid, Nanotechnology, Information Technology, Communication and Control, Environment, and Management (HNICEM), 2020: IEEE, pp. 1-6.

[24] I. I. Litvinov, V. A. Titov, and A. S. Trofimov, "The Development of Artificial Neural Network for Restoration of the Waveform of Secondary Current Distorted by Current Transformer Saturation," in 2022 5th International Youth Scientific and Technical Conference on Relay Protection and Automation (RPA), 20-21 Oct. 2022 2022, pp. 1-14, doi: 10.1109/RPA57581.2022.9951103.

[25]	 Reza Taghipour Gorji, Seyyed Mehdi Hosseini, Ali Akbar Abdoos, and Ali Ebadi, "A hybrid intelligent method for compensation of current transformers saturation based on PSO-SVR," Periodica Polytechnica Electrical Engineering and Computer Science, vol. 65, no. 1, pp. 53-61, 2021.

[26]	 Zahra Babaei and Mohamad Moradi, "Novel method for discrimination of transformers faults from magnetizing inrush currents using wavelet transform," Iranian Journal of Science and Technology, Transactions of Electrical Engineering, vol. 45, pp. 803-813, 2021.

[27]	 Christian Laurano, Sergio Toscani, and Michele Zanoni, "A simple method for compensating harmonic distortion in current transformers: Experimental validation," Sensors, vol. 21, no. 9, p. 2907, 2021.

[28]	 Makarand Sudhakar Ballal, Manish Ganesh Wath, and Hiralal Murlidhar Suryawanshi, "Measurement current transformer error compensation by ANN methodology," Journal of The Institution of Engineers (India): Series B, vol. 101, pp. 261-271, 2020.

[29] 	Sopheap Key, Vattanak Sok, Sun-Woo Lee, Chang-Sung Ko, Soon-Ryul Nam, and Nam-Ho Lee, "Current transformer saturation compensation based on autoencoder and deep learning," in 2020 IEEE Power & Energy Society General Meeting (PESGM), 2020: IEEE, pp. 1-5.

[30] 	Dharmesh Patel and Nilesh Chothani, "Evaluation of various dynamics on current transformer saturation with a model study on power system protection," in Recent advances in Power Systems: Select Proceedings of EPREC 2022: Springer, 2023, pp. 121-136.

[31]	 Ning Tong et al., "Extra‐sensitive impedance differential protection immune to CT saturation," IET Generation, Transmission & Distribution, vol. 14, no. 25, pp. 6142-6157, 2020.

[32]	 Teratam Bunyagul, Peter Crossley, and Phil Gale, "Overcurrent protection using signals derived from saturated measurement CTs," in 2001 Power Engineering Society Summer Meeting. Conference Proceedings (Cat. No. 01CH37262), 2001, vol. 1: IEEE, pp. 103-108.

[33]	 T. Bunyagul, PA Crossley, and P Gale, "Design and evaluation of an overcurrent relay suitable for operation with measurement current transformers," 2001.

[34] Jiao, Xingchao, and Taiying Zheng. "Remanent flux detection method for a protection current transformer based on fluxgate theory." International Journal of Electrical Power & Energy Systems 155 (2024): 109591.

[35] Li, S., Bai, L., Zhang, X., Tian, L., Zhang, J., Liu, Z., & Chen, C. (2024). A defect opening profile reconstruction method based on multidirectional magnetic flux leakage detection. Measurement, 233, 114701.

[36]	 P. Suksirithawornkul, S. Premrudeepreechacharn, T Kasirawat, and S Sirisumrannukul, "Optimal microgrid controller design of a hybrid microgrid for Khun Pae village in Thailand," Int. J. Smart Grid Clean Energy, vol. 10, pp. 57-68, 2020.

[37] N. Charbkaew and T. Bunyagul. (2010). Enhanced differential protection algorithm immune to distorted current signals. Ph.D. E-Dissertation Book, King Mongkut's University of Technology North Bangkok, Bangkok, Thailand, 2010.

[38] Teratam Bunyagul, Noppadol Charbkaew, Peter Crossley and Thanachat Thanasettagone, “Testing of the Saturation Detector Algorithm,” in Proc. Asia-Pacific Protection & Testing Conference, Malysia, 2012.

[39]	 Praditpong Suksirithawornkul, Teratam Bunyagul, Noppadol Charbkaew, Yotaka Chompusri, Tirapong Kasirawat, and Narong Tantichayakorn, "Analysis and Experimental Study in a Load Break Switch for a Smart Distribution System," in 2020 2nd International Conference on Smart Power & Internet Energy Systems (SPIES), 2020: IEEE, pp. 105-110.