Resilience quantification and mitigation cost analysis for sector-coupled distribution grids under climate change impacts

Paul-Hendrik HOMBERG 	Florian HANKAMMER	Nadine LIENENKLAUS

University of Wuppertal – Germany	University of Wuppertal – Germany	University of Wuppertal – Germany

homberg@uni-wuppertal.de	hankammer@uni-wuppertal.de	lienenklaus@uni-wuppertal.de

Markus ZDRALLEK

University of Wuppertal – Germany

zdrallek@uni-wuppertal.de

Keywords: 	resilience quantification, sector coupling, distribution grids, climate change adaptation, mitigation strategies, investment analysis

# Abstract

This paper presents a method for simulating sector-coupled energy systems, quantifying their resilience and analyzing the cost-effectiveness of mitigation strategies for a broad range of scenarios. Using data from a German distribution grid operator, the study examines the impact of high-impact, low-probability events, such as heavy rainfall, on the power grid and evaluates the effectiveness of various mitigation measures, including Vehicle-to-Grid and Gas-to-Power systems, as well as traditional grid hardening methods. The simulation environment integrates detailed grid models to realistically assess different failure scenarios and their effects on system resilience. Results indicate that while conventional hardening methods are most effective in cost minimization, Vehicle-to-Grid mitigation measures significantly enhance resilience by mitigating initial impacts of disruptions. The study underscores the importance of sector-coupled mitigation strategies, particularly under future climate scenarios, and provides a comprehensive framework for evaluating energy system resilience.

# Introduction

Climate change impacts the energy system by influencing both energy demand and generation capacity while exerting pressure on the infrastructure. The growing complexity of modern energy systems, coupled with the increasing frequency and severity of climate-related events, exacerbates these challenges. The high unpredictability of future weather events further complicates assessing their potential impact on energy systems [1]. Among these, high-impact, low-probability (HILP) events, such as extreme storms or heavy rainfall, are particularly challenging due to their rarity and potential to cause widespread disruption to energy infrastructure. Therefore, it is crucial to accurately simulate the effects of HILP events, quantify their impact on the energy system, and evaluate the effectiveness of potential mitigation measures to enhance system resilience.

Sector coupling, which integrates the electricity, gas, heat, and mobility sectors, offers a promising opportunity to enhance energy system resilience by utilizing the different time constants of energy transmission, transport, and storage to improve the flexibility of the entire system. In some cases, energy flows from one sector can substitute for another during failures, stabilizing the system or mitigating disruptions entirely [2, 3]. Moreover, integrating energy storage systems in the distribution grid level can enhance resilience by reducing dependence on the overlying grid. For example, highly electrified households with renewable generation, such as photovoltaics, combined with battery storage, can achieve 



temporary autarky during outages, mitigating consequences of climate-induced grid disruptions and improving the system’s resilience from the bottom up.

To date, most research has focused exclusively on the electricity grid. Given the potential benefits of sector coupling, there is a clear need for a method to simulate sector-coupled energy systems and quantify resilience across sectors [4–7]. This paper proposes a simulation environment and a novel assessment methodology designed to bridge this gap, offering a comprehensive metric for evaluating sector-wide resilience under various scenarios. It analyzes the impact of climate change-related events using real grid data and evaluates resilience-enhancing measures by considering both associated system costs and event probabilities. The approach includes an investment analysis framework to assess the cost-effectiveness of mitigation strategies, guiding decisions on grid enhancements under current and future climate conditions. This supports sustainable energy planning by balancing resilience gains against economic investments.

# Background

Climate change poses a growing threat to electricity distribution grids, with intensifying hazards such as heavy rainfall, windstorms, extreme temperatures, and drought challenging system reliability and infrastructure integrity. These climate-induced risks necessitate a detailed understanding of their impacts on distribution networks to inform effective adaptation strategies. Equally critical is the concept of resilience, which defines a system’s ability to anticipate, absorb, adapt to, and recover from disruptions. This section first explores the potential impacts of climate change on distribution grids, detailing how specific hazards affect critical components, and then reviews the resilience literature, highlighting frameworks and metrics to enhance energy system robustness under climate stress.

## Potential climate change impacts on the distribution grid

Climate change poses a significant challenge to the resilience and reliability of electricity distribution systems. As global temperatures rise and climate patterns shift, distribution infrastructure, particularly its key components, is increasingly exposed to a wide array of climate-induced hazards. These developments are especially concerning given the essential role that distribution systems play in ensuring a stable and continuous electricity supply to residential, commercial and industrial consumers. Projections from the Intergovernmental Panel on Climate Change (IPCC) provide a framework for evaluating future climate scenarios based on varying greenhouse gas emission trajectories. Two widely used Representative Concentration Pathways (RCPs) illustrate the range of plausible futures. RCP 4.5 assumes moderate mitigation, projecting a global temperature increase of approximately 2.4 °C by 2100, whereas RCP 8.5, a high-emissions pathway, anticipates warming exceeding 4 °C by the end of the century [8]. Both paths point to a significant intensification of extreme weather events, such as heavy rainfall, storms, thunderstorms, extreme heat and cold, or periods of drought, with a direct impact on electricity distribution systems.

Electricity distribution systems are particularly vulnerable due to their wide geographic spread and the significant proportion of above-ground components vulnerable to environmental hazards. Typical systems include medium-voltage substations (MVSS), distribution cabinets, overhead lines, underground cables, and household connections, many of which were not originally designed to withstand projected climatic extremes. The physical impacts of climate change manifest themselves in a variety of weather-related hazards, each of which poses different technical and operational challenges and will be discussed in the following subsections.

### Heavy rainfall

One of the most immediate and well-documented impacts is the increased frequency and intensity of heavy rainfall events. Such events are already being observed in many regions and are expected to intensify under RCP 8.5, with direct impacts on the operability of electricity distribution equipment and systems. It is imperative to acknowledge the dual factors of surface runoff and proximity to bodies of water, which have the potential to pose significant risks to electrical distribution equipment during periods of heavy rainfall. Surface runoffs are defined as the process by which water flows across the surface of the ground after precipitation has fallen, either because it cannot be absorbed into the ground or because the capacity of local drainage systems has been exceeded. Key indicators of vulnerability to surface runoff include proximity to runoff channels, the size of associated catchment areas, flow velocities influenced by impermeable surfaces or slopes, and terrain depressions that may accumulate water. With regard to proximity to water bodies, the following risk factors must be considered: location within designated flood zones, expected flood depths, and flow velocities. The effects of these hazards vary according to the type of equipment concerned, but commonly include water ingress into current-carrying components, contamination of MVSS, mechanical damage, or even the complete displacement of equipment due to intense hydraulic forces [9].

### Wind and thunderstorm

In addition to heavy rainfall, other extreme weather phenomena, such as strong windstorms, severe thunderstorms, and convective weather events, are exerting an increasing strain on distribution system equipment. Electrical distribution infrastructure is particularly vulnerable to storm damage when topographical conditions expose infrastructure to coinciding vegetation-related hazards, such as nearby trees classified as critical. Such conditions may include hilltop locations, the absence of windbreaks, and direct exposure to treefall [10]. Thunderstorms pose additional risks, particularly to overhead lines, which are susceptible to lightning-induced surges and mechanical damage. Although the frequency of thunderstorms exhibits regional variation, the risk of lightning is found to be significantly influenced by the degree of local exposure. For instance, the presence of tall structures such as buildings, transmission towers, or trees has been shown to significantly alter the probability of lightning strikes near overhead lines [11].

### Extreme heat

Extreme heat is one of the most pervasive hazards. Elevated ambient temperatures can cause thermal overload in secondary equipment housed in MVSS and distribution cabinets. Prolonged heat exposure accelerates insulation degradation and electronic aging, increasing the likelihood of failure in sensors, relays, and communication modules [12]. Overhead conductors are subject to increased resistance and thermal expansion, resulting in higher losses, reduced ampacity, and mechanical sag. These effects can violate clearance standards and compromise system stability, especially during peak load conditions [13].

### Extreme cold

In contrast, extreme cold events, though expected to become less frequent globally, may still occur at the regional level due to changes in atmospheric circulation patterns, such as polar vortex disruptions. In regions historically unexposed to such conditions, distribution systems frequently exhibit insufficient thermal resilience. Secondary equipment housed in MVSS and distribution cabinets is particularly vulnerable to material embrittlement, condensation-induced moisture ingress, and the failure of temperature-sensitive components, including relays, sensors, and communication modules [14]. Simultaneously, overhead conductors are exposed to significant mechanical challenges due to snow and ice accretion. Increased ice loads impose substantial tensile and bending stresses on conductors, poles, cross arms, and insulators, heightening the risk of structural failures such as conductor snapping and pole collapse [15].

### Drought

Drought conditions pose a range of risks to distribution equipment, some of which are more subtle in nature, yet no less critical. A reduction in soil moisture has been shown to diminish the thermal conductivity of the ground, thereby hindering heat dissipation from underground power cables. The phenomenon of thermal build-up has been demonstrated to accelerate the process of insulation degradation, thereby increasing the likelihood of cable failure. This phenomenon is particularly salient in densely populated urban environments, where cables are subjected to conditions that are proximate to their thermal limits [16]. Furthermore, drought has been shown to increase soil resistivity, thereby impairing the performance of grounding systems essential for fault current dissipation and system safety. Elevated ground resistivity may lead to ineffective protection coordination, increased touch and step voltages, and an elevated likelihood of ground potential rise events. In extreme cases, the retrofitting or complete redesign of earthing systems may be necessary in order to maintain safety and reliability standards [17].

## Resilience

The term 'resilience' (from Latin resilire: to bounce back, to rebound) is defined in various ways depending on the context. In psychology, resilience refers to an individual's ability to overcome crises and grow from them [18]. In the technical field, it describes the ability of a system or infrastructure to maintain or quickly restore functionality during and after disruptions [19]. For energy systems, the term resilience has become increasingly prevalent, yet no universally accepted definition exists due to contextual diversity and the field’s dynamic evolution. Organizations such as CIGRE have proposed definitions, emphasizing limited system degradation post-disruption [20] but multiple definitions of technical resilience persist, each tailored to specific challenges and research objectives [4–7].

Amid diverse interpretations and methods for quantifying resilience, the resilience trapezoid, often termed the resilience curve, serves as a cornerstone for assessing system performance in energy systems. As depicted in Figure 1, this model visualizes a system’s Measure of Performance (MOP) over time, capturing the response to a disruption through distinct phases: a pre-disruption baseline, a performance drop during the disruptive phase, and a recovery phase leading to a new equilibrium [21].

Figure 1: General system response to a disturbance including typical system behavior patterns according to [4]

The shape of the resilience curve is frequently used to quantify resilience in energy systems, reflecting the system’s performance dynamics during and after disruptions [4]. The MOP often represents the proportion of customers connected to the grid, linking resilience to extreme events such as storms or technical failures. A common metric is the area under the curve, where a smaller area reflects greater resilience by indicating fewer customer outages and faster recovery. Other characteristics derived from the curve include robustness (minimum MOP, indicating resistance to degradation), rapidity (speed of recovery), and redundancy (availability of alternative resources), which provide a comprehensive assessment of system behavior across disruption and recovery phases. These metrics enable tailored evaluations of energy system resilience, particularly for HILP events [22].

Beyond MOP curve-based metrics, other resilience quantification methods include fragility curves, availability-based metrics, and network topology analysis, which assess energy system resilience to HILP events. Fragility curves model component failure probabilities under extreme conditions, while availability-based metrics evaluate system uptime or service reliability. Network topology analysis examines structural vulnerabilities in grid connectivity. These methods can be classified by system scope—distribution-level (e.g., customer-focused metrics), transmission-level (e.g., line failure probabilities), or generic (e.g., system-wide indices)—and by analytical approach, such as deterministic (fixed scenarios) or probabilistic (stochastic simulations). Probabilistic models, including Monte Carlo simulations, further quantify uncertainties in disruption impacts. These diverse approaches, while offering robust tools for resilience evaluation, underscore the need for standardized metrics to address the complexities of sector-coupled energy systems, as explored in this study. [4, 6]

# Method

This section describes the method developed to simulate energy systems, quantify their resilience, and assess the cost-effectiveness of mitigation strategies under diverse disruptions. Initially, the simulation environment is outlined, detailing the tools and models employed to replicate a wide variety of failure scenarios within realistic grid configurations. Subsequently, the resilience quantification framework is introduced, presenting a novel metric to evaluate system performance across sectors during disruptions. Finally, a mitigation cost analysis framework is proposed, incorporating economic indicators to inform investment decisions for enhancing resilience.

## Simulation environment

Selecting an appropriate simulation environment is crucial for quantifying resilience in sector-coupled energy systems. This environment must realistically model a variety of energy systems and failure scenarios while efficiently generating results within computational and simulation time constraints. For this task, a Python-based time series simulation approach, integrating open-source libraries and custom-developed code, was adopted to ensure reproducibility, maintenance, and extensibility. Figure 2 illustrates the method’s components and information flow, encompassing network calculation, resilience quantification, and mitigation cost assessment.

Figure 2: Overview of the components and information flow of the simulation environment within the method presented

To realistically model a variety of scenarios, a simulation environment based on detailed grid models has been chosen. For this task, a range of commercial and freely available software options are suitable, including programs such as STANET, SAInt, and TransiEnt. A detailed comparison of these tools can be found in [23]. The open-source network calculation programs pandapipes [23] and pandapower [24] have been selected because their coupling meets key criteria: they enable efficient calculation of coupled electricity, gas, and heating networks, offer an interface with other Python applications for access to simulation parameters, and allow extendable functionality by modifying the source code.

The network calculation module receives the modeled energy systems as input data, both in normal operation and in the event of a disruption. This includes the physical models of the networks and time series data of all operating resources for the time horizon under consideration. Cost parameters for energy procurement, distribution, taxes and penalty costs for supply interruptions are used to determine the operating cost of the respective scenario. As output data, the simulation environment provides potential and flow variables for each sector and time step, as well as the utilization of operating resources, which are essential for assessing the system’s state under extreme conditions. An overview of the operational constraints for each energy sector is provided in Table 1 and further specified in [25]. Furthermore, the costs associated with the optimal operation of the energy system are calculated for each time step. These outputs are then saved and forwarded to the resilience and mitigation cost modules to evaluate the system’s overall performance, resilience, and the cost-effectiveness of mitigation strategies.

Table 1: Excerpt of operational constraints for electricity and gas systems as accounted for in this study [25]

| Electricity | Gas |
| --- | --- |
| Current I≤Imax | Flow velocity 0≤ω≤ωmax |
| Voltage Umin≤U≤Umax | Pressure pmin≤p≤pmax |

## Resilience quantification framework

Sector-coupled energy systems exhibit complex interdependencies that challenge conventional resilience assessment methods. These systems demand a tailored approach to evaluate their capacity to withstand and recover from disruptions, particularly under HILP events. To address this, this section introduces a resilience quantification framework for sector-coupled energy systems. It begins with a definition of resilience that reflects the systems’ unique characteristics, followed by a quantification method that extends established metrics for cross-sector analysis, enabling comprehensive resilience evaluation.

### Definition

As outlined in the background section, numerous resilience definitions and assessment methods exist, with the resilience curve widely used for its ability to depict system performance during disruptions. Building on this, this paper introduces a definition and quantification method for resilience in sector-coupled energy systems. The definition encompasses key aspects of technical resilience relevant to sector-coupled energy systems. It is designed to accommodate a wide range of scenarios in sector-coupled energy systems and is compatible with the presented simulation environment. Resilience is defined as: "The ability of the energy system to maintain its function despite a disruption and to limit the duration and impact of the disruption, including the ability to anticipate, absorb, adapt, and recover quickly from such events".

### Quantification

The resilience quantification methodology extends established approaches to enable cross-sector resilience evaluations, with the MOP serving as the core metric to quantify system performance during disruptions. In this study, the MOP is defined as the ratio of the operating costs under normal conditions, denoted as Cnormal(t), to those during a disruption, denoted as Cdisruption(t), as described in Equation (1):

| MOP(t)=Cnormal(t)Cdisruption(t) | (1) |
| --- | --- |

This approach leverages the detailed cost calculations inherent to the simulation environment, where the supply task is aimed to be fulfilled with minimal costs. The choice of operating costs ratio as the MOP is driven by several key considerations. First, operating costs provide a quantifiable measure of system performance, capturing the economic efficiency of energy delivery across sectors (e.g., electricity, gas, heat). Second, during disruptions, operating costs can reflect the economic consequences of failures, including costs incurred when energy supply is interrupted or substituted through sector coupling, such as gas-to-power systems mitigating a power outage. To enhance the MOP’s ability to capture disruption impacts, Value of Lost Load (VoLL) costs are integrated as a penalty for undelivered energy, as defined in [26]. The VoLL quantifies the socioeconomic costs of supply interruptions, enabling comparison of disruption severity across sectors. This approach not only accounts for operational inefficiencies but also captures broader economic impacts, such as lost productivity, and facilitates assessment of the economic trade-offs of resilience-enhancing measures like redundancy or sector-coupled solutions.

Based on the typical response pattern shown in Figure 1, an assessment methodology is established following [27]. This methodology quantifies resilience and reflects the characteristics of anticipation, absorption, adaptation, and recovery, as mentioned in the definition and quantified in Equations (2)–(7). The robustness R is defined as the minimum of the MOP during the disturbance event, quantifying the system's absorption capacity:

| R=min(MOP(t)) | (2) |
| --- | --- |

Rapidity during the disruptive phase RAPIDP is represented by the average rate of change of the MOP between the onset of the disturbance td and the time of the minimum tr. This metric indicates the system's delay capacity:

| RAPIDP=MOPtr-MOPtdtr-td | (3) |
| --- | --- |

For the regenerative phase, rapidity RAPIRP is calculated as the average rate of change of the MOP from the time of the minimum tr to the time of reaching the new normal state tn. This reflects the ability to recover:

| RAPIRP=MOPtn-MOPtrtn-tr | (4) |
| --- | --- |

Time average performance loss TAPL describes the overall severity of the failure by integrating the area between the MOP during normal operation and the failure case, normalized to the failure duration:

| TAPL=tdtnMOPt0-MOPt dttn-td | (5) |
| --- | --- |

Recovery ability RA is represented by the MOP value in the new normal state after the failure has been resolved:

| RA=MOPtn | (6) |
| --- | --- |

Finally, the general resilience GR combines the previous metrics to represent the overall resilience of the system as a scalar value.

| GR=R∙RAPIRPRAPIDP∙TAPL-1∙RA | (7) |
| --- | --- |

Figure 3 visually represents the resilience metrics defined in Equations (2)–(7), illustrating the system’s performance dynamics through the resilience curve.

Figure 3: Resilience curve showing the measure of performance (MOP) over time, with metrics robustness R, rapidity RAPIDP, RAPIRP, time average performance loss TAPL, recovery ability RA, and general resilience GR

### Aggregation across multiple disruptions

In resilience analysis, evaluating a system based on a single fault scenario may not fully capture its ability to anticipate, absorb, adapt, and recover from a range of disruptions. For instance, a fault that stresses the system without causing supply interruptions may yield a favorable resilience score, while a slightly more severe fault could lead to significant disruptions. This sensitivity highlights the need for an integrated assessment across multiple fault scenarios, providing a more comprehensive view of the system’s resilience under diverse conditions. To address this, individual resilience curves, each representing the MOP for a specific fault scenario, are aggregated into a single MOP function. The aggregated MOP denoted MOPagg(t), is computed as a weighted average:

| MOPagg(t)=iwi∙MOPi(t)iwi | (8) |
| --- | --- |

where MOPit is the MOP for fault scenario i and wi is the weight assigned to scenario i. The weights wi may be determined based on contextual factors, such as assigning uniform weights when scenarios are deemed equally relevant or employing differentiated weights to reflect variations in scenario probability, criticality, or data reliability. From MOPagg(t), resilience metrics such as robustness, rapidity and general resilience can be derived using established definitions, providing an integrated assessment of the system's resilience across multiple faults.

## Mitigation cost analysis framework

Investing in resilience-enhancing measures for energy distribution systems necessitates a cost-benefit analysis balancing disruption impacts, economic and societal, against mitigation expenditures. These costs, spanning direct financial liabilities for distribution system operators (DSOs), such as infrastructure repair and regulatory penalties, and indirect socioeconomic damages, like productivity losses, are complex, especially for HILP events worsened by climate change. Limited data and variable stakeholder valuations further complicate quantification. This paper proposes a mitigation cost analysis framework to estimate HILP event costs and mitigation benefits, using two approaches: a total cost assessment capturing all system costs, and a direct cost assessment focusing on costs borne by DSOs, such as regulatory penalties and repair costs, offering actionable insights for DSOs, regulators, and policymakers.

### Total costs assessment

Utilizing the simulation environment, operating costs during supply disruptions in sector-coupled energy systems are computed over the period from disruption onset td to recovery tn. These operating costs include energy procurement costs borne by customers, additional costs when energy is sourced from more expensive alternatives, and VoLL costs for unserved energy. Direct equipment costs are then added to these operating costs to determine the total costs. The cost per event for a given scenario, denoted Cx, where x∈normal,  disrupted, mitigated denotes normal operation, disrupted operation without mitigation, or disrupted operation with mitigation, respectively, is defined as:

| Cx=tdtnCxtdt+Cdamage,x | (9) |
| --- | --- |

In this expression, Cxt represents the timestep-related operating cost for scenario x, and Cdamage,x accounts for direct equipment costs, including repair, replacement, and personnel expenses incurred due to equipment damage during an event. To quantify the economic impact of an HILP event, the cost increase, due to the disruption ∆Cevent, is calculated by subtracting the cost, under normal operation Cnormal, from the cost of the disrupted scenario without mitigation, Cdisrupted:

| ∆Cevent=Cdisrupted-Cnormal | (10) |
| --- | --- |

The cost avoided through the implementation of a mitigation strategy ∆Cavoided is determined by comparing the disrupted scenario without mitigation to the disrupted scenario with mitigation Cmitigated:

| ∆Cavoided=Cdisrupted-Cmitigated | (11) |
| --- | --- |

Next, by using the expected annual rate of a HILP event, derived from its return period and probability distribution, the yearly avoidable cost is calculated as:

| ∆Ca=λ∙∆Cavoided | (12) |
| --- | --- |

where ∆Ca is the expected yearly avoidable cost, λ is the expected annual rate of the event, and ∆Cavoided is the avoided cost per event, as defined in Equation (11).

The expected yearly avoidable cost ∆Ca is compared to the investment cost Cinvest of the corresponding mitigation strategy that mitigates these costs. Assuming the mitigation strategy provides this protection throughout its expected lifespan μ, the yearly avoidable costs are summed over the lifespan, with k indexing the years, and discounted using the discount rate z to obtain their present value, which is then compared to the investment cost as follows:

| Cinvest≤k=0μ∆Ca(1+z)k | (13) |
| --- | --- |

If the present value of the yearly avoidable costs exceeds Cinvest, the investment is economically viable from an economy-wide perspective, encompassing both socioeconomic and direct costs.

### Direct costs assessment

DSOs do not bear all of the systems cost such as energy procurement costs nor certain indirect socioeconomic costs that can be quantified within the VoLL. This necessitates an alternative approach to estimate their liabilities; thus, a method based on the monetary factor of the System Average Interruption Duration Index (SAIDI) is applied. In Germany, the incentive regulation ordinance defines a quality element that rewards or penalizes operators based on reliability, measured via the SAIDI. Although HILP events are currently excluded due to their force majeure classification under the current regulatory framework, the SAIDI can provide a robust basis for operator cost estimation.

Just as in the total cost assessment, the cost per event for a given scenario, denoted Cx (as defined previously), is given as:

| Cx=SAIDIx∙CSAIDI+Cdamage,x | (14) |
| --- | --- |

Here, SAIDIx is the SAIDI value for scenario x, CSAIDI is the cost per SAIDI unit as specified by the Federal Network Agency quality element regulation [26], specifically CSAIDI=m∙N, where m is the monetary factor (e.g., 0.29 €/min/customer/year), N is the number of customers, and thus CSAIDI represents the annual penalty cost per minute of interruption for the customer base (€/min/year), and Cdamage,x encompasses direct equipment costs, such as repair, replacement, and personnel expenses, incurred due to equipment damage during an event. From here, the same logic as in Equations (10)–(13) can be applied to assess whether the investment is economically viable from the DSO’s perspective. The direct costs assessment complements the cost analysis framework by focusing on operator-specific costs.

# Case study

The presented method is tested through a case study based on data from a German DSO. The area under consideration includes an urban medium-voltage electricity grid, supplying approximately 14,000 customers. Additionally, a gas grid is present in large parts of the region, to which approximately 3,700 customers are also connected. The distribution grid operator provided data on the physical infrastructure, as well as the loads and feeders, which were converted into a computable model. Customer-related data, such as the number of customers served by each MVSS, are also available. To calculate the operating costs under normal operation conditions, the currently valid procurement costs for electricity and gas for end consumers were used. In the event of a supply disruption, the interrupted supply is penalized with the VoLL costs provided by the Federal Network Agency [26], which assess the economic damage of the undelivered supply in monetary terms, along with the costs associated with equipment damage.

## Modeling climate impacts

Climate change introduces diverse and complex challenges for energy systems, complicating impact assessments. The simulation environment and evaluation methodology presented in this paper were developed to simulate and evaluate a wide range of scenarios. However, this case study specifically focuses on the effects of heavy rainfall events on the power grid, as realistic scenarios can be modeled using the available data. Gas network interruptions were excluded due to their greater resilience to heavy rainfall, attributed to underground placement, meshed topology, and partial operation without electricity [28, 29]. On the electrical side, the vulnerability assessment from [30] serves as the basis for modeling the consequences of heavy rainfall events on the power grid. This assessment evaluates the assets in the network area and quantifies their vulnerability to heavy rainfall events. The findings indicate that several MVSS are at risk of failure due to flooding during heavy rainfall events. Based on this data, 15 MVSS classified as at risk were selected to simulate the consequences of potential flooding. First, a model was built to determine the specific outage times and the occurrence times of the outages for each MVSS.

The input parameters of this model include the inferred probability of failure from the vulnerability assessment, the length of flooding periods, and the restoration time of the MVSS, which comprises personnel availability time, drying time, and repair time. To model a wide range of scenarios, multiple sets of downtimes and occurrence times were generated to reflect different scenario severities, ranging from a 10-year to a 100-year return period. Scenario 10 represents a severity that is as intense as an event expected to occur every 10 years, while scenario 100 represents a severity as intense as an event occurring every 100 years. The model outputs for downtimes of the MVSS are shown in Table 2 for the first five MVSS, sorted by vulnerability score. Although modeling HILP events with such low probabilities involves significant uncertainties, it provides valuable insights for testing the method under varied conditions and evaluating different scenarios individually.

Table 2: Downtimes (in hours) of the five most vulnerable MVSS under different scenario severities based on current (2025) climate change progression

| MVSS | 10 | 20 | 30 | 40 | 50 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | - | 22.32 | 30.24 | 38.88 | 46.80 | 92.16 |
| 2 | - | - | 26.04 | 33.48 | 40.30 | 79.36 |
| 3 | - | - | - | - | 23.01 | 46.23 |
| 4 | - | - | - | - | 23.01 | 46.23 |
| 5 | - | - | - | - | 22.47 | 45.15 |

The modeled downtimes of the MVSS in Table 2 represent a set of scenarios based on the current progression of climate change. However, it is projected that the intensity of heavy rainfall events will increase across all climate regimes as climate change progresses, with more pronounced increases expected in regions that are already wet [31]. A regional climate outlook by GERICS [32], based on RCP scenarios, projects that under the high-emission RCP 8.5 scenario, the severity of heavy rainfall events, measured at the 99th percentile of daily precipitation, will increase by 9 % for 2036–2065 and 18 % for 2069–2098 relative to the 1971–2000 baseline. These projections were used to adjust the model’s input parameters, generating MVSS downtimes and occurrence times for these future periods. For brevity, the current climate conditions are denoted as 2025, the projected climate for 2036–2065 as 2050, and the projected climate for 2069–2098 as 2075 in all subsequent figures, tables, and discussions.

## Modeling mitigation measures

Due to the limited deployment of sector-coupling technologies, sector coupling has constrained potential to enhance resilience in contemporary energy systems. To explore potential improvements, two hypothetical, explorative sector-coupling approaches of a scientific nature are modeled. Additionally, a conventional measure, which is a practical and established solution that does not rely on sector coupling, is modeled as a comparative baseline. All three mitigation measures are designed with resilience as the primary focus, with their economic viability assessed in a subsequent section.

### Vehicle-to-Grid

Vehicle-to-Grid (V2G) integrates the mobility and electricity sectors by utilizing the electrical energy stored in battery electric vehicles to mitigate supply interruptions. In this model, 30 % of households affected by a supply interruption possess a V2G-capable vehicle that is connected to the household at the time of disruption. These households can disconnect from the grid, using the vehicle as a power source. Each V2G-capable vehicle delivers a maximum power of 3.7 kW and has a usable capacity of 40 kWh. This configuration enables households to maintain energy flow during outages, provided the vehicle’s capacity and power output are sufficient to meet demand.

### Gas-to-Power

Gas-to-Power (G2P) represents the coupling of the gas grid with the electricity grid. The potential for generating electricity from gas is simulated using technologies such as fuel cells in a hydrogen network or combined heat and power generation with conventional natural gas. It is hypothetically assumed that every 10th household connected to the gas network and threatened by a supply interruption has a G2P power system capable of providing up to 5 kW of electrical power during a power supply interruption.

### Hardening of MVSS

The final mitigation measure modeled is a conventional, non-sector-coupled approach to harden MVSS. Using grid data and the vulnerability assessment [30], the two MVSS with the highest power at risk were identified. These substations were reinforced with practical measures, such as elevating critical equipment above flood levels or installing waterproof enclosures, ensuring complete protection against flooding across all scenario severities.

## Simulation

The presented heavy rainfall events, with and without climate forecast adjustments, were simulated across scenario severities ranging from 10 to 100-year return periods, both with and without the proposed mitigation measures, within the established simulation environment. All scenarios were modeled for a representative June day, the month with the highest precipitation in the region, making it a suitable period to simulate the impacts of HILP heavy rainfall events [32].

As the consequences of HILP events can exhibit pronounced time-dependence, discrete simulations are necessary to assess event-specific impacts prior to aggregation. For instance, energy systems experience variable stress from temporal demand and generation fluctuations. Peak loads amplify VoLL costs due to heightened consumption, while elevated renewable infeed during low-demand phases risks voltage limit violations. Rerouting energy flows during HILP events may overload adjacent networks. Mitigation via storage or sector-coupling might be adequate under nominal fault conditions but may fail amid peak or extreme scenarios. Thus, individual simulations are critical to elucidate these time-sensitive factors. Therefore, 24 simulations were conducted for each scenario severity, one for each hour of the day, yielding a total of 2,880 simulations across all combinations of scenario severities, mitigation methods, and climate impacts. This provides a broad scope to explore system behavior under diverse circumstances while offering a sensitivity analysis of event timing’s impact on cost and resilience.

## Aggregation of simulation results

To obtain a generalized resilience score and associated operational costs, enabling conclusions about expected system performance across a spectrum of scenario severities and mitigation strategies, a weighted aggregation method is applied as outlined in Equation (8), effectively synthesizing multiple simulation outcomes into a single, representative metric.

In this study, a variant refers to a specific combination of mitigation strategies (e.g., no mitigation, V2G, G2P, hardening) and climate change scenarios (e.g., 2025, 2050, 2075). The MOP, defined as the ratio of normal to disrupted system costs (Equation 1), is calculated for each variant v scenario severity s and hourly simulation h, denoted MOPv,s,h(t). Assuming equal likelihood of event occurrence across all hours, the MOPs,h(t) curves are averaged, with  H = 24  representing the number of hourly simulations per day, to obtain a representative result for the simulated June day:

| MOPv,s(t)=1Hh=1HMOPv,s,h(t) | (15) |
| --- | --- |

Next, the MOPv,s(t) curves, each corresponding to a specific scenario severity s, are aggregated into a single MOP for a variant, denoted MOPv(t), encompassing all scenario severities, representing a specific combination of mitigation strategies and climate change progression. In this study, heavy rainfall events are modeled using a Poisson distribution, justified by their rarity, independence, and annual homogeneity. For a Poisson process, the expected annual rate λs of events exceeding the intensity threshold for return period Ts is λs=1/Ts. However, this rate includes all events with severity s or greater, causing overlap across scenario severities. To address this, interval expectance values are defined, representing the expected annual rate of events within distinct intensity intervals Ts,Ts+1:

| λinterval,s=λs-λs+1=1Ts-1Ts+1 | (16) |
| --- | --- |

These intervals (e.g., 10-20) ensure mutually exclusive probability contributions. The aggregated MOP for the variant is then computed as a probability-weighted average:

| MOPv(t)=sλinterval,s∙MOPv,s(t)sλinterval,s | (17) |
| --- | --- |

This weighting ensures that MOPv(t) accurately reflects the system resilience across all event severities, with weights proportional to their likelihood, providing a generalized representation of the system's overall resilience.

## Cost assessment

To evaluate the costs arising from the simulated HILP heavy rainfall events and assess the investment viability of mitigation strategies, the framework outlined previously is applied, with parameters adjusted to reflect the specifics of the case study. This analysis is conducted from two perspectives: a total cost assessment, capturing socioeconomic impacts, and a direct cost assessment, focusing on operator-specific liabilities.

### Total costs assessment

The simulation environment computes timestep-related operating costs for each scenario, encompassing customer-borne energy costs (including procurement, distribution, and taxes) and the VoLL costs for unserved energy, as defined in Equation (9). Distribution network losses and inefficiencies in energy conversion from sector-coupling technologies are also incorporated into these calculations.

For each variant v, the total cost is calculated for each scenario severity and hourly simulation using Equation (9), where the scenario type (normal, disrupted, or mitigated) is determined by the variant’s mitigation strategy. Consistent with the aggregation methodology applied to the MOP curves, the total costs from the 24 hourly simulations are averaged to obtain a representative daily cost per variant and scenario severity:

| Cv,s=1Hh=1HCv,s,h | (18) |
| --- | --- |

where H = 24 represents the number of hourly simulations. This averaging assumes equal probability of event occurrence throughout the day, providing a representative daily cost for each variant and severity. The expected yearly cost for each scenario severity is then determined using the interval expectance value λinterval,s from Equation (16), which ensures disjunct probability intervals:

| Ca,v,s=λinterval,s∙Cv,s | (19) |
| --- | --- |

To calculate the total expected yearly cost for a variant v, the yearly costs across all scenario severities are summed:

| Ca,v=sCa,v,s | (20) |
| --- | --- |

Yearly cost savings from mitigation are derived by comparing the total yearly cost of a mitigated variant vmitigated to the baseline variant without mitigation vdisrupted:

| ΔCa,v=Ca,vdisrupted-Ca,vmitigated | (21) |
| --- | --- |

Finally, the economic viability of the mitigation strategy is assessed using Equation (13), assuming an expected effective lifespan of the mitigation measure of μ=40 years and a discount rate of z=6 %. If the present value of the yearly cost savings exceeds the investment cost, the mitigation strategy is considered economically viable.

### Direct costs assessment

The direct cost assessment evaluates costs borne by the DSO, such as regulatory penalties and equipment repair expenses, using the Average System Interruption Duration Index (ASIDI) as the primary metric for medium-voltage disruptions. Since disruptions at the MVSS due to heavy rainfall events are associated with the medium-voltage grid, the ASIDI, as defined by regulatory standards [33] is used:

| ASIDIv,s,h=jSj,v,s,h∙tj,v,s,hStotal | (22) |
| --- | --- |

Here, ASIDIv,s,h represents the ASIDI for variant v, scenario severity s, and hourly simulation h; Sj,v,s,his the apparent power of disrupted load j (i.e., the MVSS); tj,v,s,h is the outage duration for load j; and Stotal is the total apparent power of all loads in the grid, corresponding to the total nominal rated apparent power of the MVSS. For scenarios without mitigation, outage durations tj,v,s,h are sourced from Table 2, which lists supply interruption durations. In scenarios with mitigation, if the mitigation fully restores supply, tj,v,s,h is zero; otherwise, for partial mitigation (e.g., using V2G, G2P), Sj,v,s,h reflects the residual unmitigated power loss, with tj,v,s,h derived from the simulation environment.

The direct cost for each event is then calculated as:

| Cv,s,h=ASIDIv,s,h∙CASIDI+Cdamage,v,s,h | (23) |
| --- | --- |

Here, Cv,s,h is the total direct cost, ASIDIv,s,h is the interruption index defined above, CASIDI is the cost per unit of ASIDI, and Cdamage,v,s,h covers equipment repair costs specific to the variant, severity, and hour. These costs feed into Equations (18)–(21) to estimate yearly savings and aggregate costs, while investment viability for the DSO is assessed using Equation (13). This approach ensures a thorough financial analysis of HILP events and the value of mitigation, balancing socioeconomic and operational perspectives.

# Results and discussion

The simulation environment produces a substantial amount of data, encompassing network limit violations, operational costs, and resilience metrics across a range of scenarios, including various mitigation strategies and climate change projections. This section evaluates these outcomes, emphasizing system performance under HILP events, the efficacy of mitigation approaches, and the implications of intensifying climate change.

## Network limits and operational constraints

Operating sector-coupled energy systems under extreme conditions can lead to inadmissible operating states if energy flows from a disrupted sector are substituted by another, potentially causing cascading effects. The simulation environment assessed the potential and flow values outlined in Table 1 across all individual simulations. Results show that all operating values remained within regulatory limits. The disruption of MVSS had minimal impact on the electrical network, with a slight reduction in capacity utilization of affected power lines and a negligible voltage increase that did not affect other grid components. During G2P operation, the gas network’s capacity utilization increased marginally but remained well below capability limits, as the network is designed for higher winter demand. While these simulations confirm operational stability in terms of steady-state parameters, frequency-based dynamic simulations could further validate system stability, as a sudden load drop may impact frequency response, particularly in systems with high renewable penetration and reduced conventional inertia.

## Resilience assessment

This subsection examines the system’s resilience (its ability to anticipate, absorb, adapt to, and recover from HILP events) across varying scenario severities and mitigation variants. Resilience is quantified using the MOP, defined as the cost ratio between normal and disrupted states, with trends analyzed via aggregated resilience curves. Individual hourly simulations captured time-dependent effects, but their influence was modest. Thus, the analysis prioritizes aggregated results to highlight trends across scenarios and variants.

### Scenario severity

Figure 4 depicts resilience curves for the baseline variant (current climate, no mitigation). As the scenario severity increases, the MOP declines more steeply, indicating that a greater number of MVSS are flooded on average. Additionally, higher scenario severities are associated with longer downtimes, attributed to the extended duration of these events. After the high-water levels caused by the heavy rainfall event subside and the time required to restore the MVSS has elapsed, the MVSS are gradually switched back on.

Figure 4: Resilience curves (MOP as cost ratio) for different scenario severities under the variant current (2025) climate change progression without mitigation measures

### Mitigation strategies and climate change

Figure 5 presents the aggregated scenario severities across all considered variants, showing resilience curves as MOP cost ratios averaged over multiple heavy rainfall simulations. All curves typically decline sharply at the event’s onset, as MVSS flood in quick succession after heavy rainfall begins. The V2G variants are the exception, where system function is partially maintained until battery storage capacity is depleted, delaying the MOP drop. Comparing G2P variants to those without mitigation, the G2P variants noticeably mitigate the MOP decrease. This is due to G2P systems’ ability to partially take over energy flows. Unlike V2G, G2P systems sustain these flows without storage capacity limits, but their initial mitigation impact is less pronounced due to their less extensive distribution. In contrast, conventional hardening variants (abbreviated as hard.), which reinforce the MVSS with the highest power at risk, mitigate most consequences. These MVSS, critical for their large load and long flooding durations, significantly influence the MOP decline. Furthermore, resilience curves for advancing climate change (2050 and 2075) show worse outcomes compared to current (2025) conditions. The 2075 variants stand out with particularly low MOP values, especially in lower severity scenarios, as more MVSS are disrupted by the rising intensity of heavy rainfall events.

Figure 5: Resilience curves (MOP as cost ratio) for the aggregated scenario severities across all considered variants

### Resilience quantification

Table 3 presents the GR values for scenarios under current climate change progression. The system without mitigation measures (none) performs worst, with the lowest aggregated GR score, labeled as total GR (0.73), indicating a limited capacity to absorb impacts of heavy rainfall events compared to variants with mitigation measures. The V2G mitigation measure achieves the highest total GR (2.91), excelling in the scenario severity with a 20-year return period (8.44) due to its ability to delay initial disruption and mitigate short supply disruption impacts most effectively through battery storage. The G2P measure slightly improves the total GR (0.86) over the baseline by leveraging sustained energy flows, though its effect remains less pronounced across scenarios due to sparse deployment, partly due to the necessary presence of the gas network, and its inability to absorb initial impacts. Conventional hardening completely mitigates consequences for scenario severities with 20–40-year return periods by protecting the two MVSS affected by heavy rainfall events. However, in more severe scenarios, its effectiveness is reduced, for example, to 0.13 for the 100-year return period, as additional MVSS fail without further mitigation to limit disruption consequences.

Table 3: General resilience values (GR) for different scenario severities for variants under current (2025) climate change progression

| Variant | 20 | 30 | 40 | 50 | 100 | Total |
| --- | --- | --- | --- | --- | --- | --- |
| none | 2.73 | 0.61 | 0.45 | 0.33 | 0.06 | 0.73 |
| V2G | 8.44 | 1.48 | 1.00 | 1.31 | 0.41 | 2.91 |
| G2P | 3.25 | 0.68 | 0.50 | 0.42 | 0.09 | 0.86 |
| hard. | - | - | - | 8.71 | 0.13 | 1.99 |

## Cost and investment decisions

With climate change intensifying the frequency and severity of HILP events like heavy rainfall, understanding the economic implications for sector-coupled energy systems becomes essential for effective resilience planning. This section presents results from the proposed cost assessment framework to evaluate the financial impacts of such disruptions on distribution grids. The total cost assessment quantifies system-wide operating cost increases, including energy procurement and penalties for unserved energy. It evaluates these across various mitigation strategies and climate scenarios (2025, 2050, 2075). In contrast, the direct cost assessment estimates the hypothetical liabilities of the DSO, such as regulatory penalties tied to the ASIDI and equipment repair costs, despite current exemptions for HILP events. This framework provides critical insights into the cost-effectiveness of resilience-enhancing investments, and the following subsections detail these assessments, supported by tables and figures, to guide policymakers and DSOs in balancing resilience with economic viability.

### Total costs assessment

Table 4 presents total operating cost increases from heavy rainfall events under current (2025) climate conditions, comparing mitigation strategies against a no-mitigation baseline for selected scenario severities. Costs, calculated via Equation (10), peak at 2.64 €M in scenario severity 100 without mitigation. The conventional hardening method, reinforcing the two MVSS with the highest power at risk, cuts costs to 1.78 €M by preventing disruptions at these vulnerable MVSS. V2G and G2P strategies yield similar reductions in milder scenarios (e.g., 0.08 €M in scenario severity 20), but V2G’s 1.98 €M cost in scenario severity 100 reflects storage depletion during prolonged outages, while G2P’s sustained gas supply lowers costs to 1.56 €M. The ‘-’ entries indicate no MVSS failures, hence no costs.

Table 4: Total operating cost increases (in €M) for different scenario severities for variants with current (2025) climate change progression

| Variant | 10 | 20 | 30 | 40 | 50 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| none | - | 0.09 | 0.33 | 0.42 | 0.77 | 2.64 |
| V2G | - | 0.08 | 0.30 | 0.41 | 0.60 | 1.98 |
| G2P | - | 0.08 | 0.30 | 0.39 | 0.58 | 1.56 |
| hard. | - | - | - | - | 0.26 | 1.78 |

The increasing costs of future climate change are shown in Table 5, comparing no-mitigation costs under current (2025) conditions with projections for 2050 (2036–2065) and 2075 (2069–2098). Intensified rainfall increases costs, especially in milder scenarios. For scenario severity 20, costs triple from 0.09 €M in 2025 to 0.29 €M in 2075, driven by an 18 % rise in rainfall intensity, affecting more MVSS. In contrast, scenario 100 costs grow modestly from 2.64 €M to 2.83 €M, as most vulnerable MVSS are already impacted, with increases tied to longer outages.

Table 5: Total operating cost increases (in €M) for different scenario severities for variants without mitigation methods under 2025, 2050, and 2075 climate conditions

| Variant | 10 | 20 | 30 | 40 | 50 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| 2025 | - | 0.09 | 0.33 | 0.42 | 0.77 | 2.64 |
| 2050 | - | 0.09 | 0.34 | 0.45 | 1.15 | 2.74 |
| 2075 | - | 0.29 | 0.35 | 0.81 | 1.59 | 2.83 |

To inform investment decisions, the annual expected costs of all simulated scenario severities are calculated based on their likelihood of occurrence, aggregated, and discounted to derive the total present value of annual expected avoidable loss costs. These costs are visualized in Figure 6, where the left y-axis displays the annual costs, which decrease over time due to discounting, and the right y-axis shows the cumulative total. The cumulative value indicates the total expected costs avoided by each mitigation strategy, facilitating a direct comparison with the installation costs of the mitigation measures. Figure 6 indicates that the MVSS hardening method, reinforcing two substations with 100 % protection against heavy rainfall, justifies a 350,000 € investment under the 2025 climate scenario, provided it remains effective for its 40-year lifespan. In contrast, the V2G strategy supports a 190,000 € investment, mitigating the consequences of MVSS failure by supplying energy locally. Overall, Figure 6 highlights that the MVSS hardening method, as a targeted approach to protect against heavy rainfall, yields the highest cost savings across all climate scenarios, followed by G2P and V2G methods, which can address the consequences of disruptions from any kind, however in the limited scope of heavy rainfall events they fall behind the hardening method. Additionally, the progression of climate change increases the present value of annual expected avoidable loss costs, with the 2075 variants showing the highest cost increases due to the disruption of additional MVSS that remain unaffected in the 2025 climate variants, showing the growing economic impact of climate change.

### Direct costs assessment

The direct cost assessment in this study presents hypothetical costs linked to the DSO, calculated using the ASIDI penalty as a cost component, as described in the previous chapter. Currently, German DSOs are not liable for these costs, as ASIDI increases resulting from HILP events are excluded from the reported ASIDI due to their classification as force majeure events. However, if DSOs were held accountable, as with regular supply disruptions, these costs would apply, serving as a key metric for assessing potential future liabilities.

Table 6 shows the resulting ASIDI increases from HILP events. It can be seen that the ASIDI values escalate with rising scenario severity, where the no-mitigation variant rises from 9 to 312 minutes by scenario severity 100, while MVSS hardening reduces this to 210 minutes. At this point, the G2P variant lowers ASIDI to 184 minutes, as its constant and broadly applied power supply exceeds the power loss mitigated by the MVSS hardening method, applied only to two substations.

Table 6: ASIDI increases (in min) for different scenario severities for variants with current (2025) climate change progression

| Variant | 10 | 20 | 30 | 40 | 50 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| none | - | 9 | 27 | 34 | 72 | 312 |
| V2G | - | 8 | 25 | 32 | 57 | 234 |
| G2P | - | 8 | 24 | 31 | 54 | 184 |
| hard. | - | - | - | - | 25 | 210 |

Table 7 shows direct cost increases, comprising ASIDI penalties and equipment damage costs, across scenario severities in 2025 climate conditions. Costs closely correlate with ASIDI, as higher ASIDI values reflect both greater interruption penalties and increased equipment damage: for example, the no-mitigation variant rises from 0.05 €M in scenario severity 20 to 1.49 €M in scenario severity 100, while hardening reduces this to 1.03 €M, outperforming V2G (1.16 €M) , though G2P performs better at 0.94 €M. This correlation highlights ASIDI’s critical role in direct costs, informing DSO mitigation strategies.

Table 7: Direct operating cost increases (in €M) for different scenario severities for variants with current (2025) climate change progression

| Variant | 10 | 20 | 30 | 40 | 50 | 100 |
| --- | --- | --- | --- | --- | --- | --- |
| none | - | 0.05 | 0.13 | 0.17 | 0.36 | 1.49 |
| V2G | - | 0.04 | 0.13 | 0.16 | 0.29 | 1.16 |
| G2P | - | 0.04 | 0.12 | 0.15 | 0.28 | 0.94 |
| hard. | - | - | - | - | 0.14 | 1.03 |

Figure 7 shows the total present value of annual expected avoidable direct costs for each mitigation method across different climate variants. The mitigation methods exhibit a similar performance trend to the total cost assessment in Figure 6: the targeted MVSS hardening method mitigates the greatest amount of costs, followed by G2P and V2G, which perform less effectively. However, the direct cost values are lower than those in Figure 6 for the 2025 climate variant; MVSS hardening justifies up to 166,000 € over its 40-year lifespan, while V2G supports up to 93,000 €. This reduction arises because direct costs exclude additional expenses included in total costs, such as energy procurement or conversion inefficiencies when energy is supplied from other sectors. Additionally, the ASIDI-based monetary factor for direct costs is lower than the VoLL used in total costs, as it averages a mix of customer types, including industrial, which are less penalized, while the simulated area’s high residential penetration drives higher VoLL costs.

Figure 6: Total annual and cumulative present value of avoidable costs (in €) over 100 years for mitigation strategies (MVSS hardening, V2G, G2P) across climate scenarios (2025, 2050, 2075) discounted at 6%

Figure 7: Direct annual and cumulative present value of avoidable costs (in €) over 100 years for mitigation strategies (MVSS hardening, V2G, G2P) across climate scenarios (2025, 2050, 2075) discounted at 6%

# Conclusion

This study advances the understanding of climate change impacts on electricity distribution grids by developing a framework for assessing the resilience of sector-coupled energy systems, with a focus on HILP events such as heavy rainfall. The proposed methodology, integrating a tailored resilience definition, a quantitative assessment approach, and a Python-based simulation environment, enables a holistic evaluation of electricity, gas, and heating systems. By incorporating a cost assessment framework, the study provides a tool for analyzing the interplay between resilience and economic considerations under diverse climate scenarios.

Testing across varied event severities, mitigation strategies, and climate projections revealed that intensifying climate change increases operational costs, particularly as extreme weather events become more severe. Conventional grid hardening, such as reinforcing MVSS, emerged as the most cost-effective strategy for mitigating specific hazards like heavy rainfall. Conversely, sector-coupled solutions, notably V2G systems, demonstrated superior resilience by absorbing initial disruption impacts, as quantified by the General Resilience (GR) metric. These findings highlight the complementary roles of targeted and cross-sectoral approaches in enhancing system resilience and cost-effectiveness.

The framework's practical utility lies in its ability to guide DSOs and policymakers in prioritizing resilience-enhancing investments. For instance, DSOs can use the cost assessment to justify funding for MVSS upgrades, while policymakers can leverage the resilience metrics to develop regulations promoting sector-coupling technologies like V2G. This is particularly critical as climate change amplifies the need for adaptive energy systems, aligning with global sustainability goals.

Despite uncertainties in modeling HILP events, this study establishes a foundation for resilience assessment in sector-coupled grids. Future research will explore how enhanced sector coupling, combined with greater integration of renewable energy and energy storage, can further strengthen resilience, particularly in innovative operational concepts such as cellular energy systems. Moreover, the framework can be used to analyze other HILP events, including other climate-related events, across electricity, gas, and heating networks to provide a comprehensive assessment of climate impacts on distribution grids. By offering a scalable and adaptable tool, this research contributes to the development of resilient, sustainable energy systems capable of addressing the challenges of climate change.

# Acknowledgments

Funded by the Deutsche Forschungsgemeinschaft 
(DFG, German Research Foundation) – 511806895

References

[1]	A. T. D. Perera, V. M. Nik, D. Chen, J.-L. Scartezzini, and T. Hong, "Quantifying the impacts of climate change and extreme climate events on energy systems," Nature Energy, vol. 5, no. 2, pp. 150–159, 2020, doi: 10.1038/s41560-020-0558-0.

[2]	A. Senkel, C. Bode, and G. Schmitz, "Quantification of the resilience of integrated energy systems using dynamic simulation," Reliability Engineering & System Safety, vol. 209, p. 107447, 2021, doi: 10.1016/j.ress.2021.107447.

[3]	X. Li, X. Du, T. Jiang, R. Zhang, and H. Chen, "Coordinating multi-energy to improve urban integrated energy system resilience against extreme weather events," Applied Energy, vol. 309, p. 118455, 2022, doi: 10.1016/j.apenergy.2021.118455.

[4]	P. Gasser et al., "A review on resilience assessment of energy systems," Sustainable and Resilient Infrastructure, vol. 6, no. 5, pp. 273–299, 2021, doi: 10.1080/23789689.2019.1610600.

[5]	B.-J. Jesse, H. U. Heinrichs, and W. Kuckshinrichs, "Adapting the theory of resilience to energy systems: a review and outlook," Energy, Sustainability and Society, vol. 9, pp. 1–19, 2019.

[6]	A. Umunnakwe, H. Huang, K. Oikonomou, and K. R. Davis, "Quantitative analysis of power systems resilience: Standardization, categorizations, and challenges," Renewable and Sustainable Energy Reviews, vol. 149, p. 111252, 2021.

[7]	J. Jasiūnas, P. D. Lund, and J. Mikkola, "Energy system resilience–A review," Renewable and Sustainable Energy Reviews, vol. 150, p. 111476, 2021.

[8]	V. Masson-Delmotte et al., "Summary for policymakers," 2021.

[9]	M. Dumas, B. Kc, and C. I. Cunliff, "Extreme weather and climate vulnerabilities of the electric grid: a summary of environmental sensitivity quantification methods," Oak Ridge National Lab.(ORNL), Oak Ridge, TN (United States).

[10]	T. Dokic et al., "Risk assessment of a transmission line insulation breakdown due to lightning and severe weather," in 2016 49th Hawaii international conference on system Sciences (HICSS), pp. 2488–2497.

[11]	G. M. Karagiannis et al., "Climate change and critical infrastructure–storms," Publications Office of the European Union, Luxembourg, 2019.

[12]	J. Al Rashid, L. Saintis, M. Koohestani, and M. Barreau, "Coupling simulation and accelerated degradation model for reliability estimation: Application to a voltage regulator," Microelectronics Reliability, vol. 138, p. 114682, 2022.

[13]	D. M. Greenwood et al., "A comparison of real-time thermal rating systems in the US and the UK," IEEE Transactions on Power Delivery, vol. 29, no. 4, pp. 1849–1858, 2014.

[14]	B. Keane, G. Schwarz, and P. Thernherr, "Electrical equipment in cold weather applications," in Industry applications society 60th annual petroleum and chemical industry conference, pp. 1–7.

[15]	K. Ji, X. Rui, L. Li, F. Yang, and G. McClure, "Dynamic response of iced overhead electric transmission lines following cable rupture shock and induced ice shedding," IEEE Transactions on Power Delivery, vol. 31, no. 5, pp. 2215–2222, 2016.

[16]	P. Ocłoń, "The effect of soil thermal conductivity and cable ampacity on the thermal performance and material costs of underground transmission line," Energy, vol. 231, p. 120803, 2021.

[17]	V. M. N. Dladla, A. F. Nnachi, and R. P. Tshubwana, "Analysis of varying soil resistivity on substation earthing design and performance using ETAP," in 2022 30th Southern African Universities Power Engineering Conference (SAUPEC), pp. 1–6.

[18]	A. S. Masten, "Ordinary magic: Resilience processes in development," American psychologist, vol. 56, no. 3, p. 227, 2001.

[19]	C. S. Holling, Resilience and stability of ecological systems: International Institute for Applied Systems Analysis Laxenburg.

[20]	E. Ciapessoni, D. Cirio, A. Pitto, M. van Harte, and M. Panteli, "Power System Resilience: definition, features and properties," Cigré Science & Engineering Journal, vol. 30, 2023.

[21]	R. Francis and B. Bekera, "A metric and frameworks for resilience analysis of engineered and infrastructure systems," Reliability Engineering & System Safety, vol. 121, pp. 90–103, 2014.

[22]	S. Afzal, H. Mokhlis, H. A. Illias, N. N. Mansor, and H. Shareef, "State‐of‐the‐art review on power system resilience and assessment techniques," IET Generation, Transmission & Distribution, vol. 14, no. 25, pp. 6107–6121, 2020.

[23]	L. Thurner et al., "Pandapower—An Open-Source Python Tool for Convenient Modeling, Analysis, and Optimization of Electric Power Systems," IEEE Transactions on Power Systems, vol. 33, no. 6, pp. 6510–6521, 2018, doi: 10.1109/TPWRS.2018.2829021.

[24]	D. Lohmeier, D. Cronbach, S. R. Drauz, M. Braun, and T. M. Kneiske, "Pandapipes: An Open-Source Piping Grid Calculation Package for Multi-Energy Grid Simulations," Sustainability, vol. 12, no. 23, 2020, doi: 10.3390/su12239899.

[25]	M. Koralewicz, Neue Energie aus Wuppertal/Integrierte Simulation gekoppelter Strom-, Gas-und Wärmesysteme: epubli, 2023.

[26]	Bundesnetzagentur, "Bericht zur Bestimmung des Qualitätselements 2025," Bonn, Germany, Nov. 2024. [Online]. Available: https://​www.bundesnetzagentur.de​/​

[27]	C. Nan and G. Sansavini, "A quantitative method for assessing resilience of interdependent infrastructures," Reliability Engineering & System Safety, vol. 157, pp. 35–53, 2017, doi: 10.1016/j.ress.2016.08.013.

[28]	A. C. R. Gonçalves, X. Costoya, R. Nieto, and M. L. R. Liberato, "Extreme weather events on energy systems: a comprehensive review on impacts, mitigation, and adaptation measures," Sustainable Energy Research, vol. 11, no. 1, p. 4, 2024.

[29]	C. Shao, M. Shahidehpour, X. Wang, and B. Wang, "Integrated Planning of Electricity and Natural Gas Transportation Systems for Enhancing the Power Grid Resilience," IEEE Transactions on Power Systems, vol. 32, no. 6, pp. 4418–4429, 2017, doi: 10.1109/TPWRS.2017.2672728.

[30]	F. Hankammer, N. Lienenklaus, M. Zdrallek, and F. Aschenbroich, "Topographical assessment of electrical distribution system vulnerability to heavy rainfall events," in IET Conference Proceedings CP882, pp. 128–132.

[31]	H. Tabari, "Climate change impact on flood and extreme precipitation increases with water availability," Scientific reports, vol. 10, no. 1, p. 13768, 2020.

[32]	GERICS, "Klimaausblick Remscheid und angrenzende Landkreise," Hamburg, Germany, 2025. [Online]. Available: www.gerics.de

[33]	"IEEE Guide for Electric Power Distribution Reliability Indices," IEEE Std 1366-2022 (Revision of IEEE Std 1366-2012), 2022, doi: 10.1109/IEEESTD.2022.9955492.