Improved phase comparison distance protection for transmission lines of energy storage power stations based on polarization voltage phase reconstruction

Haoyu Zhu, Xiaoran Wang, Chunju Fan, Yan Hu, Nengling Tai

Abstract—Affected by the different fault characteristics of electrochemical energy storage power stations under charging and discharging operating states, the phase comparison distance protection using positive sequence voltage as polarization voltage may operate incorrectly if faults occur in the forward direction of the energy storage side protection and the reverse direction of the system side protection. Therefore, an improved distance protection scheme that can adapt to both charging and discharging states of is studied. Firstly, the fault characteristics of the energy storage station under different charging or discharging states are analyzed, and the influence mechanism of fault characteristics on phase comparison distance protection operation performance was discussed. On this basis, an improved scheme for distance protection based on polarization voltage phase reconstruction was proposed. Finally, verification was conducted on the PSCAD/EMTDC simulation platform. The simulation results show that the proposed scheme can effectively reduce the impact of fault characteristics of energy storage power stations. The sensitivity and reliability of phase comparison distance protection are effectively improved under different charging and discharging states and transition resistance conditions.

Index Terms—Energy storage, phase comparison distance protection, polarization voltage， phase reconstruction

I. INTRODUCTION

I

N recent years, the scale of electrochemical energy storage in China has developed rapidly [1]. According to statistics from the National Energy Administration, by the end of 2024, the cumulative installed capacity of energy storage projects nationwide reached 73.76 million kWh/168 million kWh, an increase of more than 130% from the end of 2023, and showed a trend of centralization and large-scale [2].

Electrochemical energy storage is typically connected to the grid through power electronic converters, Its fault characteristics exhibit features such as limited short-circuit current amplitude, current phase control, and uncertain equivalent impedance [3-4]. In addition, the fault characteristics of energy storage are also affected by the charging and discharging states, which are different from other inverter-based sources like wind power and photovoltaics [5-6]. These characteristics make the distance protection performance issues of the transmission lines in energy storage stations more significant compared to those in wind power and photovoltaic stations.

Current research on the performance of distance protection for inverter-based power supply transmission lines mostly focuses on wind power and photovoltaic power stations [8-11], without involving the special fault characteristics of energy storage power stations during charging states. Reference [8] analyzed the applicability of phase-comparison distance protection based on the fault characteristics of doubly fed wind generator (DFIG), but the fault characteristics of DFIG differ significantly from those of inverter-based sources such as photovoltaic power and energy storage systems. Reference [10] analyzed the inverter-side distance protection performance when a short circuit fault occurs in inverter-based power supply transmission lines. The results show that due to the existence of zero-sequence current, the inverter side distance protection can correctly identify most ground faults but cannot correctly identify two-phase short circuit faults. Reference [11] proposed a new measured impedance expression for two-phase ground faults, but it requires the use of communication. Although the above research results can improve the performance of distance protection on the transmission lines of wind power and photovoltaic stations to a certain extent, whether it can adapt to the transmission lines of energy storage power stations still needs to be further verified, due to the significant difference in short-circuit current phase characteristics between charging and discharging states.

There are relatively few studies on distance protection for the transmission lines of energy storage power stations [13-15]. Among them, references [13] and [14] analyzed the influence mechanism of energy storage converter control methods, current limiting strategies, and charging/discharging states on short-circuit current characteristics during transmission line faults, but no relevant analysis on the applicability of phase-comparison distance protection was found. Reference [15] studied the applicability of power directional components in both charging and discharging operating modes of energy storage, but similarly did not involve the adaptability of phase-comparison distance protection.

In addition to the power frequency distance protection mentioned above, many studies have utilized high-frequency components [16-18] or power frequency variation to design distance protection schemes. Among them, high-frequency distance protection is more susceptible to interference from high-frequency signals such as noise, compared to power frequency distance protection, and its application requires upgrading measurement devices. As for power frequency variation distance protection, its operating range is significantly affected by system impedance, line length, and load, and it is prone to the risk of maloperation during external faults [20].

Based on the above research status, this paper first analyzes the fault characteristics of energy storage power stations under different states of charge and discharge according to the technical specifications for grid-connected electrochemical energy storage power stations[21]. Then, the adaptability of traditional phase comparison distance protection (PCDP) for the transmission line of energy storage power station is analyzed. Based on the analysis, an improved phase comparison distance protection based on polarization voltage phase reconstruction is proposed for transmission lines of energy storage power stations. Finally, the effectiveness of the proposed method is verified by simulation. Simulation results show that the proposed method can effectively reduce the impact of energy storage station fault characteristics on the PCDP. The sensitivity and reliability of the PCDP are effectively improved under different charging and discharging states and transition resistance conditions.

II. Characteristic Analysis of transmission line Faults of Energy Storage Power Stations

- A. Energy storage converter control strategy

For the current grid-connected energy storage, its converter control strategy usually adopts a dual closed-loop control method with a power outer loop and a current inner loop [22]. During a fault, the energy storage system injects positive sequence reactive current into the grid, while negative sequence current is suppressed and the amplitude of short-circuit current is limited.

Regarding the positive sequence active component of short-circuit current, no specific provisions are made in specification [21]. In current engineering practice, the active component of short-circuit current supported by energy storage tends to remain consistent with the direction before the fault, that is, the energy storage control strategy will keep its pre-fault charging and discharging state unchanged as much as possible.

The above control strategy is detailed as follows:

According to the specifications [21], the reactive current during energy storage faults is set as shown in  and  to meet the required dynamic reactive power support capability of the energy storage system:

Where:  and  are the positive sequence and negative-sequence reactive current reference values, respectively;  is the per-unit value of the positive sequence voltage at the grid connection point;  is the maximum allowable output current of the energy storage converter, with a value of ;  is the rated output current value;  is a constant coefficient greater than or equal to 1.5, taken as 1.5 in this paper.

In current engineering practice, the energy storage control strategy will keep its pre-fault charging and discharging state unchanged as much as possible. Therefore, the active component of the energy storage short-circuit current is in the opposite direction to the positive sequence voltage at the grid connection point during charging, and in the same direction as the positive sequence voltage at the grid connection point during discharging. In this paper, the magnitude of the active component of the energy storage short-circuit current is specified as  and.

where  is the active current before the fault.  and  are the reference values of positive and negative sequence active currents, respectively.

- B. Short-circuit current characteristics of energy storage

Under the control strategy described in Section 1.1, the phase relationship between short-circuit current and positive sequence voltage under different charging and discharging states is shown in Figure 1.

Fig. 1. Characteristics of short-circuit current of energy storage

In Figure 1,  and  are the phase currents in the discharge and charge states, respectively.  and  are the corresponding reactive components of the short-circuit current, whose magnitudes are determined by ;  and  are the corresponding active components of the short-circuit current, whose magnitudes are determined by equation;  and  are the angles by which the phase currents lag behind the positive sequence voltage at the grid connection point. It is worth noting that  and  are in opposite directions, so when  varies,  varies in the range of 0~90°, while  varies in the range of 90°~180°.

- C. Impedance characteristics of energy storage

The performance of the PCDP is closely related to the output characteristics of the backside power source at the protection installation location. If the power supply on the back side of the protection is a synchronous generator, its equivalent impedance is stable after the transmission line fault, thus the PCDP has stable operating characteristics. If the backside power source is an energy storage station, due to the influence of the converter control strategy, its output characteristics exhibit impedance features with significant nonlinearity and time-varying properties. In this case, the traditional backside power source impedance calculation method based on variation reflects the transient impedance characteristics determined by the control strategy [22].

- D. Verification of energy storage fault characteristics

Fig. 2.  Model topology for fault characteristics verification

A PSCAD simulation model is established according to the topology shown in Fig. 2 to verify the energy storage fault characteristics. The parameters of each component are as follows. The rated capacity of the energy storage station is 200MW, and the limiting value is taken as 1.5 times the rated current. The rated voltage of the transmission line is 220kV, with a total length of 80km. The positive and negative sequence impedances are 0.074+j0.42Ω/km, and the zero sequence impedance is 0.22+j1.26Ω/km. The positive sequence and zero-sequence capacitance parameter are 0.0086μF/km and 0.0061μF/km, respectively. The equivalent impedance of the external system is 6+j34Ω. In Figure 2, k1, k2, and k3 correspond to the backside fault of the M-side protection, the internal fault of line MN, and the external fault of the N-side protection respectively.

First, set k2 at the midpoint of line MN. An A-B interphase short circuit occurs at k2 at t=1.5s and lasts for 1s. The phase difference between positive sequence voltage and positive sequence current under different charging and discharging states of energy storage is shown in Figure 3.

Fig. 3. Phase difference between positive sequence voltage and current on the energy storage side

As shown in Figure 3(a), during the energy storage discharge mode, the phase difference between the positive sequence voltage and positive sequence current on the energy storage side varies within the range of 0~90°, but that varies within the range of 90~180° during the charging mode. This is because the direction of the active short-circuit current changes, which is consistent with the analysis in section A.

To verify the impedance characteristics of energy storage, k2 was set at 1km, 40km, and 79km from bus M, denoted as F1, F2, and F3 respectively. In the simulation, A-B interphase short circuit were set at F1, F2, and F3 at t=1.5s, lasting for 1s. The equivalent impedance amplitudes of energy storage and external system calculated by traditional method are shown in Figure 4(a) and Figure 4(b), while the equivalent impedance angle is shown in Figure 4(c). The equivalent impedance angle of energy storage under different charging and discharging states is shown in Figure 4(d).

(a) Magnitude of the equivalent impedance of energy storage

(b) Magnitude of the equivalent impedance of external system

(c) The equivalent impedance angle of energy storage and external systems

(b) The equivalent impedance angle of energy storage under different charging and discharging states

Fig. 4. Simulation results of energy storage impedance characteristics

Comparing Figure 4(a) and (b), it can be seen that the equivalent impedance amplitude of energy storage changes with fault conditions, which is different from the stable equivalent impedance of traditional power supplies. In addition, due to the limited amplitude of short-circuit current, the equivalent impedance of energy storage is much greater than that of traditional power supply. As can be seen from Figure 4(c), the change of fault conditions will not affect the equivalent impedance angle of the traditional power supply but will significantly change that of energy storage. As can be seen from Figure 4(d), the charging and discharging state will significantly affect the equivalent impedance angle of energy storage. The equivalent impedance angle of energy storage is an obtuse angle during charging but an acute angle during discharging.

In summary, the phase of the energy storage short-circuit current is significantly affected by the pre-fault charge and discharge state, and the equivalent impedance amplitude and phase angle are related to the fault conditions, and there is no stable value. Due to the limited amplitude of energy storage short-circuit current, the amplitude of energy storage equivalent impedance is much greater than that of the system.

III. Adaptability analysis of the PCDP

The PCDP is often used in renewable energy station transmission lines due to its clear directionality, and its action equation is shown in Equation .

In,  and  are the measured voltage and measured current respectively, and for the interphase distance relay, , ;  are the setting impedance;  is the polarization voltage;  is usually recorded as the operation voltage or the compensation voltage.

As a key parameter, the polarization voltage directly affects the action characteristics of the PCDP [7]. Since the measured voltage drops to zero or near zero when a metallic fault occurs near the protection, the measured voltage cannot be used as a reference voltage to avoid losing the phase comparison basis, which creates the risk of protection malfunction or rejection. In practical engineering, for asymmetric faults, the positive sequence voltage is often selected as the reference voltage to avoid this dead zone problem. This paper selects the PCDP with positive sequence voltage as the polarization voltage for adaptability analysis.

- A. Forward direction short-circuit fault analysis

Taking line MN in Figure 2 as an example, assuming a metallic short-circuit fault occurs between phases A and B at a certain point on MN, the adaptability of  is analyzed respectively at the energy storage side (M side) and the system side (N side).

    - System-side (N-side) protection

For system side protection, the equivalent diagram and its related parameters are shown in Figure 5.

Fig. 5. N-side equivalent diagram with a short-circuit on the forward direction of the N-side protection

Denoting the phase comparison result in  as ,  can be simplified according to .

In ,  is the positive sequence measured voltage on the N side;  is the fault point voltage, which is 0 under metallic fault;  is the measured current on side N;  is the line impedance from bus N to the fault point;  is the setting impedance. When a fault occurs within the protection range, , and  can be simplified to .

For traditional power sources,  is approximately equal to the line impedance angle , so the phase comparison result  equals , and the protection can operate normally. Conversely, if a fault occurs outside the protection range, the phase comparison result is 0, and the protection does not operate correctly.

    - Energy storage side (M-side) protection

For energy storage side protection, the equivalent diagram and its related parameters are shown in Figure 6.

Fig. 6. M-side equivalent diagram with a short-circuit on the forward direction of the M-side protection

Since the fault type is an inter-phase metallic fault and the energy storage side suppresses negative-sequence current, can be simplified according to .

In Equation (8),  and  are the positive sequence voltage and normal current at the fault point. In the case of interphase metallic failure, . If the fault location is within the protection range, then  can be calculated according to .

Based on the analysis in section 1.2, when the difference in voltage amplitude at the grid connection point caused by different charging and discharging states is ignored,  can be further simplified to.

Regardless of whether the energy storage is in charging and discharging state,  is always an acute angle, which causes  to gradually approach the 90° operating boundary of  during discharge, and to gradually approach the 270° operating boundary of  during charge, reducing protection sensitivity. It is worth noting that due to , the protection performance in the discharge state will be slightly better than in the charge state.

Similarly, if the fault occurs outside the protection range,  can be simplified to .

Through similar analysis, it is found that the controlled phase characteristics of energy storage short-circuit current will lead to a decrease in protection reliability during external faults.

- B. Reverse direction short-circuit fault analysis

    - System side (N-side) protection

When a metallic fault occurs on the backside of the system side protection, the equivalent diagram and its related parameters are shown in Figure 7.

Fig. 5. N-side equivalent diagram with a short-circuit on the reverse direction of the N-side protection

At this time, the N-side short-circuit current is provided by energy storage, and  can be simplified to .

Following a similar analysis, it can be found that regardless of whether the energy storage is in a charging or discharging state, the short-circuit current phase control characteristics of energy storage will cause  to deviate from the center of the action area. Furthermore, due to the influence of the line impedance angle, the protection performance problem will be more serious in charging state than in discharging state.

    - Energy storage side (M-side) protection

When the metallic fault occurs on the backside of the energy storage side protection,  can be simplified to .

At this time, the short-circuit current of the bus M is provided by the system resource,  is approximately equal to 0, and the protection will not malfunction.

IV. Improved phase comparison distance protection based on polarization voltage phase reconstruction

The analysis in Chapter III reveals that the performance issues of the PCDP mainly caused by the phase-controlled short-circuit current of energy storage. To address the issue, an improved phase comparison distance protection based on polarization voltage phase reconstruction (IPCDP) is proposed, which is suitable for the transmission lines of energy storage power stations. Since the amplitude of the equivalent impedance of energy storage differs significantly from that of system-side resources, the IPCDP first uses the equivalent impedance of the backside system to identify whether the fault occurs in the forward or reverse direction of the protection, preventing maloperation during reverse faults. For faults occurring in the forward direction, the phase of the polarization voltage is reconstructed as the sum of measured current and line impedance angle, which can eliminate the influence of the phase-controlled energy storage short-circuit current and improves the protection sensitivity and reliability. Taking the protection of line MN shown in Figure 2 as an example, the specific content of the IPCDP is explained.

- A. Forward and reverse fault identification

For M-side protection, when a fault occurs on line MN (forward direction), the equivalent impedance calculated from the M-side measured voltage and current variation reflects the impedance characteristics of the energy storage. From Section D of Chapter II, it can be seen that the equivalent impedance amplitude is very large at this time. However, when a fault occurs between the energy storage and bus M (reverse protection), the equivalent impedance reflects the sum of the line MN impedance and the system equivalent impedance, which is much smaller than the energy storage equivalent impedance.

Similarly, for N-side protection, when a fault occurs in the forward direction of the protection, the equivalent impedance calculated from the N-side measured voltage and current variation reflects the impedance characteristics of the external system. When a fault occurs in the reverse direction of the protection, the equivalent impedance reflects the impedance characteristics of the energy storage, which is much larger than the external system impedance.

Based on the above analysis, when  holds, the fault occurs in the forward direction of the protection M, otherwise it is in the reverse direction; when  holds, the fault occurs in the forward direction of the protection N side, otherwise it is in the reverse direction.

In  and ,  is the reliability coefficient, and this paper takes 1.5.  and  are the equivalent impedances of bus M and bus N to the external system, respectively.

- B. Enhanced fault identification capability in the forward direction of protection

For faults in the forward direction of protection, by reconstructing the polarization voltage phase in  to the phase of , the modified criterion shown in  can be obtained.

Similar to the analysis of , for metallic faults in the forward direction, the phase comparison result after polarization voltage phase reconstruction is 180° (within the protection zone) or 0° (outside the protection zone), which can improve protection sensitivity and avoids protection rejection due to the phase-controlled short-circuit current.

The action logic of the IPCDP is shown in Figure 9.

Fig. 9. Action logic of the IPCDP

V. Simulation verification

The adaptability analysis results of the PCDP and the effectiveness of the IPCDP proposed in this paper are verified in the model shown in Figure 2, with the same model parameters as in Chapter I Section D. The setting impedance  is set based on 85% of the outgoing line, which is 5.032+j28.56Ω. For the M-side protection,  in  is set to the sum of equivalent impedance of the external system and the impedance of line MN, which is 11.032+j62.56Ω. In ,  is set to the equivalent impedance of the external system, which is 6+j34Ω. The reliability coefficient  in  and  is set to 1.5.

- A. Adaptability verification of the PCDP

    - Forward direction fault of M-side protection

In the simulation, k2 in Figure 2 is set at 1km, 64km, and 79km from bus M, with an AB phase-to-phase metallic short circuit occurring at the k2 location at 1.5s. Simulations are conducted under two different states of energy storage: charging and discharging. The M-side phase comparison angle corresponding to  are shown in Figure 10.

(a) Charging state

(b) Discharging state

Fig. 10. Phase comparison angle of energy storage side protection under forward fault

As shown in Figure 10(a), when the energy storage is in charging state, the phase comparison result of metallic faults within the protection area is already close to the action zone boundary, posing a significant risk of protection rejection. When the fault location is located at the end of the line (79km away from the M bus), that is, outside the protection range, that is, outside the protection range, the phase comparison result is also close to the boundary of the action area, and there is a greater risk of malfunction.

As shown in Figure 10(b), if the energy storage is in discharging state, although the PCDP can identify the fault, the phase comparison result significantly deviates from the center of the action zone during internal faults, and significantly deviates from the center of the non-action area during external faults, which may lead to insufficient sensitivity and reliability of the protection.

In addition, comparing Figure 10(a) and (b), it can be found that the performance of the PCDP in discharging state is slightly better than that in charging state, which is consistent with the analysis conclusion in Chapter III.

    - Forward direction fault of N-side protection

In the simulation, k2 in Figure 2 is set at 1km, 64km, and 79km from bus N, with an AB phase-to-phase metallic short circuit occurring at the k2 location at 1.5s. Simulations are conducted under two different states of energy storage: charging and discharging. The N-side phase comparison angle are shown in Figure 11.

Fig. 11. Phase comparison angle of external system side protection under forward fault

As shown in Figures 11(a) and (b), for conventional power supplies, the phase comparison result remains stable at about 180° during internal faults and at about 0° during external faults, regardless of charging or discharging states, , and have good performance.

    - Reverse direction fault

In the simulation, an AB phase-to-phase metallic short circuit occurring at positions k1 and k3 in Figure 2 at 1.5s, respectively. k1 and k3 represent reverse direction faults for the energy storage side protection and system side protection, respectively. Simulations are conducted under two different states of energy storage: charging and discharging. The phase comparison results of the system side protection and energy storage side protection under both states are shown in Figure 12(a) and (b).

Fig. 12.  Phase comparison angle under reverse direction fault

Comparing Figures 12(a) and (b), it can be seen that when a fault occurs on the reverse direction of the energy storage side protection, the short-circuit current at bus M is provided by the external system, so the phase comparison result remains stable around the center of the non-action zone (0°) during both charging and discharging states, ensuring the protection does not malfunction. However, when the fault occurs on the reverse direction of the system side protection, the short-circuit current at bus N is provided by the energy storage, and the phase comparison results during both charging and discharging states significantly deviate from the center of the non-action zone. Moreover, the phase comparison result during the charging state approaches the boundary of the operating zone, indicating a high possibility of malfunction.

In summary, the phase-controlled characteristics of energy storage short-circuit current will significantly reduce the sensitivity and reliability of the PCDP and will lead to a more obvious performance degradation during energy storage charging.

- B. Validation verification of the IPCDP

    - Forward fault and reverse fault identification

For the M-side protection, the setting value of  in  is 11.032+j62.56Ω. Select k2 in Figure 2 at a distance of 1km from bus M, and the AB phase-to-phase metallic fault occurs at 1.5s at the k1 and k2 positions in the simulation. The equivalent impedance amplitude of the back-side system calculated by M-side measurements is shown in Figure 13(a).

For the N-side protection, the setting value of  in  is 5.032+j28.56Ω. Select k2 in Figure 2 at a distance of 1km from bus N, and the AB phase-to-phase metallic fault occurs at 1.5s at the k2 and k3 positions in the simulation.

Fig. 13.  Forward fault and reverse fault identification

For the M-side protection,  is 103.05Ω. As can be seen from Figure 13(a), when a fault occurs in the forward direction of the M-side protection (i.e., at position k2), the equivalent impedance reflects the impedance characteristics of energy storage, which is much larger than . Therefore, it can be determined from  that the fault at this time is a forward-direction fault for the M-side protection. Conversely, when the fault occurs at position k1, the equivalent impedance of reflects the impedance characteristics of external system, approximately 68.61Ω, which is significantly smaller than the setting value. Therefore, it can be determined as a reverse-direction fault. Similarly, as can be seen from Figure 13(b), the forward and reverse direction faults of N side protection can also be accurately determined by .

    - Verification of enhanced forward fault identification capability

Under the fault condition of Section A, the performance of the IPCDP proposed in this paper on the energy storage side (M side) and the system side (N side) are shown in Figure 14(a) and Figure 14(b), respectively.

Fig. 14. Forward fault identification capability of the IPCDP

Comparing the phase comparison results in Figure 14 with those of the PCDP under the same fault conditions in Figures 10 and 11, it can be seen that the method proposed in this paper can correct the phase comparison results of internal metallic faults to the center of the action area under any charging or discharging state, and correct that of external faults to the center of the non-action area, thereby maximizing protection sensitivity and reliability.

- C. Ability of the IPCDP to resist transition resistance

    - The effect of transition resistance on the ability to identify forward and reverse faults

In order to test the influence of transition resistance on the forward and reverse fault identification ability of the IPCDP, simulation verification is conducted taking the energy storage side as an example, which is relatively more difficult to distinguish. In the simulation, In the simulation, the fault occurs at 1km away from point M (k2) and the back of the protected line (k1). The fault type is set to be A-B fault, and the transition resistance is 5Ω, 10Ω and 20Ω, respectively.

TABLE I

Identification of forward and reverse faults under different transition resistances

| Fault location | Charging and discharging state | Transition resistance /Ω | Equivalent impedance amplitude /Ω | Recognition results |
| --- | --- | --- | --- | --- |
| k1 (Reverse Direction) | Charge | 5 | 68.61 | Correct |
|  |  | 10 | 68.61 | Correct |
|  |  | 20 | 68.61 | Correct |
|  | Discharge | 5 | 68.61 | Correct |
|  |  | 10 | 68.61 | Correct |
|  |  | 20 | 68.61 | Correct |
| k2 (Forward Direction) | Charge | 5 | 394.69 | Correct |
|  |  | 10 | 400.89 | Correct |
|  |  | 20 | 409.35 | Correct |
|  | Discharge | 5 | 575.34 | Correct |
|  |  | 10 | 541.92 | Correct |
|  |  | 20 | 486.07 | Correct |

As shown in Table I, when a fault occurs in the reverse direction of the M-side protection , the equivalent impedance calculated by M-side measurement quantity is always the set impedance , which is independent of the transition resistance.

Therefore, the reverse-direction fault of M-side protection is always correctly identified. For forward direction faults of M-side protection, the equivalent impedance varies slightly with different transition resistances. However, since the amplitude of the short-circuit current from the energy storage is always limited, the equivalent impedance is always much greater than the set impedance, and the identification result of  is always correct.

    - The effect of transition resistance on the sensitivity of M-side protection

In the simulation, faults are set at 40km and 79km from bus M along line MN (i.e., at the midpoint and end of the line). The performance of the IPCDP is shown in Table Ⅱ.

TABLE Ⅱ

M-side protection performance under different transition resistances

| Fault location | Charging and discharging state | Transition resistance /Ω | /DEG | Identification results |
| --- | --- | --- | --- | --- |
| 40km from M | Charge | 5 | 198.3 | Action |
|  |  | 7.5 | 222.1 | Action |
|  |  | 10 | 256.9 | Action |
|  | Discharge | 5 | 122.5 | Action |
|  |  | 7.5 | 108.1 | Action |
|  |  | 10 | 98.4 | Action |
| 79km from M | Charge | 5 | 347.4 | No action |
|  |  | 7.5 | 338.8 | No action |
|  |  | 10 | 335.2 | No action |
|  | Discharge | 5 | 63.8 | No action |
|  |  | 7.5 | 71.3 | No action |
|  |  | 10 | 75.3 | No action |

As shown in Table 2, for the M-side protection, although the transition resistance may affect the phase comparison result, the method proposed in this paper can still ensure correct fault identification when the transition resistance is 10 Ω.

    - The effect of transition resistance on the sensitivity of N-side protection

In the simulation, faults are set at 40km and 79km from bus N along line MN (i.e., at the midpoint and end of the line). The performance of the IPCDP is shown in Table Ⅲ.

TABLE Ⅲ

N-SIDE PROTECTION PERFORMANCE UNDER DIFFERENT TRANSITION RESISTANCES

| Fault location | Charging and discharging state | Transition resistance /Ω | /DEG | Identification results |
| --- | --- | --- | --- | --- |
| 40km from N | Charge | 5 | 166.7 | Action |
|  |  | 7.5 | 169.2 | Action |
|  |  | 10 | 162.8 | Action |
|  | Discharge | 5 | 172.2 | Action |
|  |  | 7.5 | 165.4 | Action |
|  |  | 10 | 158.4 | Action |
| 79km from N | Charge | 5 | 30.1 | No action |
|  |  | 7.5 | 40.6 | No action |
|  |  | 10 | 49.4 | No action |
|  | Discharge | 5 | 29.5 | No action |
|  |  | 7.5 | 34.6 | No action |
|  |  | 10 | 38.5 | No action |

As can be seen from Table Ⅲ, compared to the energy storage side protection, the system side protection performance is less affected by the transition resistance. For phase-to-phase faults with transition resistance within 10 Ω, the IPCDP can correctly identify.

VI. Conclusion

This paper studies the fault characteristics of the energy storage power stations transmission lines and its influence on the traditional phase comparison distance protection, under different charging and discharging operating conditions. An improved phase comparison distance protection based on polarization voltage phase reconstruction is proposed. The main conclusions of the paper are as follows:

(1) The phase of energy storage short circuit current differs significantly under charging and discharging conditions. Traditional phase comparison distance protection has performance issues in both charging and discharging states of energy storage, with more severe problems during the charging state. Even under the condition of metallic fault, there is still a high risk of rejection for energy storage side protection if the fault occurs in its forward direction If the fault occurs in the reverse direction of the system side protection, there is a high risk of maloperation for the system side protection.

(2) The IPCDP proposed in this paper makes full use of the characteristic that the amplitude of energy storage short circuit current is limited and uses the amplitude of back-side equivalent impedance to determine whether the fault occurs in the forward or reverse direction of the protection, which can effectively avoid the problem of protection maloperation during reverse direction faults.

(3) By reconstructing polarization voltage phase, the IPCDP proposed in this paper can maximize protection sensitivity and reliability under interphase metallic fault conditions and has sufficient capability to resist transition resistance.

References

- Tang Xisheng, Li Wei, Shen Xiaodong. Research progress and prospect of energy storage planning method for new power system [J]. Automation of Electric Power Systems, 2024, 48(9):178-191(in Chinese).

- National Energy Administration. Operation of renewable energy grid connection in 2024［EB/OL］. (2025-01-21) ［2027-01-21］. https://www.nea.gov.cn/20250221/e10f363cabe3458aaf78ba4558970054/c.html(in Chinese)

- A. Haddadi, M. Zhao, I. Kocar, U. Karaagac, K. W. Chan and E. Farantatos, "Impact of Inverter-Based Resources on Negative Sequence Quantities-Based Protection Elements," in IEEE Transactions on Power Delivery, vol. 36, no. 1, pp. 289-298, Feb. 2021.

- Chao Chenxu， Zheng Xiaodong， Gao Piao， et al． Adaptive distance protection for transmission line of photovoltaic station during asymmetric short circuit[J]． Proceedings of the CSEE， 2022， 42(18) ： 6681-6693(in Chinese) ．

- Y. Fang, K. Jia, Z. Yang, Y. Li, and T. Bi, “Impact of inverter-interfaced renewable energy generators on distance protection and an improved scheme,” IEEE Trans. Ind. Electron., vol. 66, no. 9, pp. 7078–7088, Sep. 2019.

- K. El-Arroudi and G. Joos, “Performance of interconnection protection based on distance relaying for wind power distributed generation,” IEEE Trans. Power Del., vol. 33, no. 2, pp. 620–629, Apr. 2018.

- B. Brusilowicz and N. N. Schulz, "Polarizing Voltage Generating Method for Distance and Directional Protection Elements," in IEEE Transactions on Power Delivery, vol. 36, no. 1, pp. 74-83, Feb. 2021

- Wang Xingguo, Yu Su, Zhou Zexin, et al. Action Analysis of AC Line Distance Protection Considering New Energy Power Control Response [J]. Power System Technology, 2024, 48(09):3834-3843(in Chinese).

- Zhou Zexin, Yu Su, Li Yong, et al. Analysis of the Incorrect Operation Mechanism of the Phase Comparison Distance Protection Caused by the Change of Power Angle in the Scenario of MMC-HVDC Connected Renewable Power System [J]. Proceedings of the CSEE,2023,43(05):1730-1739(in Chinese).

- A. Hooshyar, M. A. Azzouz and E. F. El-Saadany, "Distance Protection of Lines Emanating from Full-Scale Converter-Interfaced Renewable Energy Power Plants—Part I: Problem Statement," in IEEE Transactions on Power Delivery, vol. 30, no. 4, pp. 1770-1780, Aug. 2015.

- A. Hooshyar, M. A. Azzouz and E. F. El-Saadany, "Distance Protection of Lines Emanating from Full-Scale Converter-Interfaced Renewable Energy Power Plants—Part II: Solution Description and Evaluation," in IEEE Transactions on Power Delivery, vol. 30, no. 4, pp. 1781-1791, Aug. 2015.

- Y. Liang, Y. Ren and W. He, "An Enhanced Current Differential Protection for AC Transmission Lines Connecting MMC-HVDC Stations," in IEEE Systems Journal, vol. 17, no. 1, pp. 892-903, March 2023.

- HUO Qidi, TANG Xiaojun, MA Shiying, et al. Mechanism and algorithm of short circuit current in AC system affected by BESS under asymmetric short circuit faults[J]. Electric Power Automation Equipment, 2022, 42(3):153-160(in Chinese).

- BERGER M, KOCAR I, FARANTATOS E, et al. Modeling of Li-ion battery energy storage systems (BESSs) for grid fault analysis[J]. Electric Power Systems Research, 2021,196.

- Li Chao, Li Borui, Li Bin, et al. Adaptability Analysis of Power Directional Elements in Electrochemical Energy Storage Power StationsConnected to Distribution Networks [J]. Automation of Electric Power Systems,2025,49(11):126-135(in Chinese).

- Z. Yang, K. Jia, Y. Fang, Z. Zhu, B. Yang and T. Bi, "High-Frequency Fault Component-Based Distance Protection for Large Renewable Power Plants," in IEEE Transactions on Power Electronics, vol. 35, no. 10, pp. 10352-10362, Oct. 2020.

- X. Zheng et al., "High-Frequency Fault Analysis-Based Pilot Protection Scheme for a Distribution Network with High Photovoltaic Penetration," in IEEE Transactions on Smart Grid, vol. 14, no. 1, pp. 302-314, Jan. 2023.

- L. Qu, B. Hou, Z. Yang, L. Xia, H. Li and Y. Li, "An Enhanced Impedance Trajectory-Based Adaptive Distance Protection for Renewable Energy Systems," 2024 IEEE 8th Conference on Energy Internet and Energy System Integration (EI2), Shenyang, China, 2024.

- S. Yu, Z. Zhou, X. Wang, Q. Cheng, S. Wang and J. Liu, "Adaptability Analysis of Power Frequency Variation Distance Protection for AC-side of Receiving-end Converter of Offshore Wind Power MMC-HVDC System," 2022 4th International Conference on Smart Power & Internet Energy Systems (SPIES), Beijing, China, 2022.

- Qian Guoming, Chen Fufeng, Li Ling, et al. A New Algorithm for Industrial Frequency Variation Distance Protection Based on Distributed Parameter Model [J]. Automation of Electric Power Systems,2011,35(20):78-80+87(in Chinese).

- GB/T 34120-2023, Technical requirements for power conversion system of electrochemical energy storage system[S].

- C. Chao, X. Zheng, Y. Weng, Y. Liu, P. Gao and N. Tai, "Adaptive Distance Protection Based on the Analytical Model of Additional Impedance for Inverter-Interfaced Renewable Power Plants During Asymmetrical Faults," in IEEE Transactions on Power Delivery, vol. 37, no. 5, pp. 3823-3834, Oct. 2022

Haoyu Zhu received the M.Sc degrees in Electrical Engineering from Shanghai Jiao Tong University, China, in 2019 and then worked as a PhD candidate until now.

His research interests include power system protection, renewable energy and microgrid automation and power system optimal configuration.

Xiaoran Wang graduated from Hohai University in 2022 with a bachelor's degree in Electrical Engineering, and then entered the Department of Electrical Engineering at Shanghai Jiao Tong University to pursue a Master's degree in Electrical Engineering.

His research focuses on Relay Protection in New Energy Access Systems and Grid-connected energy storage technology.

Chunju Fan received the Ph.D. degree from Shanghai Jiao Tong University, China, in 2005.

She is currently an associate professor of Electrical Engineering, Shanghai Jiao Tong University. Her research interests include power system relay protection, power system fault analysis and smart grid.

Yan Hu is currently an associate professor of Electrical Engineering, Shanghai Jiao Tong University. His research interests include smart grid fault analysis, microgrid control and protection, intelligent substations and power system information security.

Nengling Tai received the Ph.D degrees in Department of Power Systems and Automation, Huazhong University of Science and Technology, China, in 2000.

He is currently a distinguished professor of Shanghai Jiao Tong University and serving as deputy dean of the Smart Energy College of Shanghai Jiao Tong University. His research interests include smart grid protection, integrated energy system optimization, ship power system optimization design and ship power system protection technology.

This work was supported by National Natural Science Foundation of China(No. 52337006).

Haoyu Zhu is with the College of Smart Energy, University of Shanghai Jiao Tong (e-mail: zhy119031910026@sjtu.edu.cn ).

Xiaoran Wang is with the Schoool of Electronic Information and Electrical engineering, University of Shanghai Jiao Tong. (e-mail: wxrwljj0301@sjtu.edu.cn ).

Chunju Fan is with the Schoool of Electronic Information and Electrical engineering, University of Shanghai Jiao Tong. (e-mail: fanchunju@sjtu.edu.cn).

Yan Hu is with the Schoool of Electronic Information and Electrical engineering, University of Shanghai Jiao Tong. (e-mail: yanhu@sjtu.edu.cn ).

Nengling Tai is with the College of Smart Energy, University of Shanghai Jiao Tong (e-mail: nltai@sjtu.edu.cn).

.