A modified current differential protection for transmission line connected to energy storage plant based on adaptive phase compensation

Haoyu Zhu, Xiaoran Wang, Chunju Fan, Yan Hu, Nengling Tai

Abstract—In current engineering practice, the phase of the short-circuit current provided by a grid-connected energy storage plant is affected by the pre-fault status of charging and discharging. When energy storage encounters a fault in the transmission line during charging, the phase difference is likely to be large between the short-circuit current it provides and the short-circuit current provided by the grid on the other side of the line, leading to a risk of no-trip failure in traditional current differential protection (CDP). To address the above problems, this paper proposes a modified current differential protection criterion based on adaptive phase compensation (MCDP). By judging the state of energy storage charging and discharging state as well as the presence of negative sequence currents, current phases on both sides of the line will be compensated at different angles, so as to reduce the phase difference and improve the sensitivity of the protection without reducing the reliability. The performance test of the MCDP is carried out through PSCAD simulation. The results show that the MCDP has good performance under different fault conditions and ability to resist fault resistance.

Index Terms—Energy storage, current differential protection, phase compensation, charging and discharging state

I. INTRODUCTION

T

HE current national standards in China for the fault ride-through capability of grid-connected energy storage, photovoltaic and direct-drive wind turbines are basically the same [1]-[3]. Therefore the steady-state reactive component of the short-circuit current of energy storage, photovoltaic and direct-drive wind turbines are basically the same during the occurrence of faults on their transmission lines. However, the standard does not specify the active component of the short-circuit current during a fault, which makes the short-circuit current characteristics of energy storage quite different compared to other inverter-based power supplies, because energy storage has both charging and discharging states.

For the fault ride-through control strategy of energy storage, in the current engineering practice, the converter control system will not change the charging and discharging state of the energy storage within the relay protection operation time on the basis of meeting the national standards. Therefore, if a fault occurs on the transmission line when the energy storage is charging, the direction of the positive sequence active short-circuit current of energy storage will remain consistent with that before the fault. This may lead to an excessive short-circuit current phase difference, resulting in a risk of no-action failure for traditional current differential protection (CDP).

The short-circuit current characteristics of discharging energy storage are similar to those of other inverter-type power sources. Currently, there has been researches on the differential protection of inverter power source transmission lines [4]-[9]. Differential impedance was introduced in [4]-[5], but this method has high requirements for data synchronization. Reference [6] proposed a combined current and voltage braking principle to improve traditional current differential protection, which can improve the protection sensitivity. However the paper only analyzed the situation when the short-circuit current phase difference is lower than 120°, which cannot cover the range when the energy storage is charging. Reference [7] proposed a current differential protection based on amplitude comparison by utilizing the characteristics that the short-circuit current of grid is much larger than that of inverter power source, but this method still suffers from the lack of sensitivity when capacity of the renewable energy plant is large. Reference [8] constructed a new differential protection principle by combining different phase currents on both sides of the line, but this method is based on the assumption of three-phase symmetry of the short-circuit current on the inverter side. Reference [9] proposed a current differential protection scheme based on the d-axis, but this scheme is not applicable to the charging energy storage. In addition, there are also some methods using indicators such as cosine similarity[10]-[12] and Pearson correlation coefficient to identify faults[13]-[14]. These methods used a data-driven approach to avoid traditional protection performance issues caused by renewable energy sources, but outliers may have a significant impact on them.

The fault current characteristics of charging-state energy storage are similar to the rectification-mode converter station. There have been studies focusing on the performance of current differential protection in this case [15]-[16]. Reference [15] proposed an adaptive current differential criterion based on current amplitude and phase compensation for energy storage. However, the meanings and selection principles of the constant coefficients in the amplitude compensation function and phase compensation function mentioned in the text were not explained, and there was no analysis or simulation on whether this criterion would cause maloperation of protection during external faults. Reference [16] proposed an enhanced current differential protection based on modifying the magnitude ratio and phase difference of currents on the two sides of the line. This method can effectively improve the performance of current differential protection, but due to the need to ensure reliability during external faults, it still lacks sufficient sensitivity when applied to internal faults with current amplitude ratios close to 1.

This paper firstly analyzes the short-circuit current characteristics of the energy storage plant and its influence on the performance of the CDP, and proposes a modified current differential protection for transmission line of energy storage plant based on adaptive phase compensation. By judging the state of energy storage charging and discharging state as well as the presence of negative sequence currents, current phases on both sides of the line will be compensated at different angles, so as to improve the sensitivity of the protection without reducing the reliability.

II. Characteristics Of Short-circuit Current Of Energy Storage And Its Impact On The CDP

  - Characteristics of short-circuit current of energy storage

The control strategy of the energy storage plant analyzed in this paper adopts common double closed-loop control method with power outer loop and current inner loop. Similar to other inverter-type power supply, the amplitude of short-circuit current of energy storage plant is limited and phase is controlled[17]-[19]. However, compared with photovoltaic and other inverter-type power supply, energy storage exists in the charging state, and the direction of the active component of the short-circuit current is affected by the charging and discharging state before the fault.

    - Dynamic reactive support

The current national standard in China requires grid-connected energy storage to inject positive sequence reactive current into the grid during faults, and to absorb negative sequence reactive current when the fault type is asymmetrical in order to reduce negative sequence voltage. This article sets the reactive current during energy storage faults as follows, referencing the current standards [3]:

When a symmetrical fault occurs, the energy storage should inject reactive current into the grid connection point, with the magnitude shown in ：

Among them,  is the per unit value of the phase voltage at the AC port of the energy storage inverter,  is the dynamic reactive current coefficient, which takes a value of 1.5-3, and this paper takes 1.5.  is the reactive current at the grid connection point of the energy storage converter, and  is the rated output current value of the AC port of the energy storage converter.

When an asymmetrical fault occurs, the energy storage shall inject positive sequence reactive current into the grid point and absorb negative sequence reactive current with the following magnitudes:

andare the positive and negative sequence reactive currents at the energy storage grid connection point；and are the positive and negative sequence dynamic reactive current coefficients, not less than 1, this paper takes 1.5; and  are the positive and negative sequence voltage per unit values at the grid connection points of the energy storage converters, respectively.

    - Affected by charging and discharging state before failure

In the current engineering practice, the converter control system will not change the charging and discharging state of the energy storage within the relay protection operation time.

Based on the above characteristics, the magnitude of the active component of the energy storage short-circuit current in this article is specified as formula. The direction of the active component of the charging and discharging state is shown in Figure 1.

In (4),  is the active current before the fault.

In case of asymmetrical fault, the control target for negative sequence active current is 0, and the magnitude of positive sequence active current is the value  shown in .

Fig. 1. Characteristics of short-circuit current of energy storage

Figure 1 shows the different relationship under charging and discharging conditions between short-circuit current of energy storage and voltage of the grid connection point.  and  are the positive-sequence active components of energy storage short-circuit current under charging and discharging conditions, respectively. The directions of  and  are opposite during charging and discharging states, resulting in a significant phase difference between phase currents  and .

  - Performance analysis of the CDP

The structure of the grid-connected system of the energy storage plant is shown in Figure 2. The performance of the CDP is analyzed by taking the protection 3 and 4 corresponding to line QN as an example. The criterion of the CDP in the form of percentage differential protection is shown in .

Fig. 2. Grid-connected system structure of energy storage plant

Where,  and  are the phase currents of the protection 3 and 4, and the positive direction is the bus pointing to the line; is the slope, which varies for different line protection devices, usually ranging from 0.6 to 0.8. The absolute value of the sum of  and  is differential current, and the absolute value of the difference between  and  is restraining current.

The ratio of the differential current over the restraining current multiplied by the slope is denoted as , which is shown in . The ratio of the short-circuit current amplitudes on both sides of the line ( and ) is denoted as  and the phase difference of them is denoted as .

Equation  can be simplified to  according to the cosine theorem.

In , .  takes different values in different protection devices, and the corresponding current differential protection has different action ranges. The boundary curves of  when  and  are shown in Figure 3. and the dashed area represents the protected no-action area.

From Figure 3, it can be seen that if  and the current amplitude ratio ,the protection can operate normally regardless of the phase difference. As the current amplitudes on both sides of the line gradually approach each other, that is,  approaches 1, the impact of phase difference  on protection also becomes increasingly significant. When , the protection will encounter a no-trip failure if the phase difference is over 102°. If , the no-action area of the CDP is significantly reduced. The effect of the phase difference can be ignored when .

Fig. 3. Boundaries of the CDP with different

In the system shown in Figure 2, if the fault resistance is not high, the short-circuit current provided by the main grid is far greater than that from the energy storage side. At this time,  is very small, and the impact of  on CDP does not need to be considered. As the fault resistance increases, the magnitude of the short-circuit current on the system side decreases, whereas the magnitude of the short-circuit current on the energy storage side is not significantly affected due to the control strategy, so  increases significantly. In this case, the effect of  on the CDP increases significantly. Therefore, for the transmission line of energy storage plant, if the energy storage is charging, there is a greater risk of no-trip failure for the CDP.

III. Modified Current Differential Protection Based On Adaptive Phase Compensation And Its Setting Method

From the analysis in Section 2, it can be seen that when the energy storage plant is charging, if a fault occurs in the transmission line, the phase difference of short-circuit current on both sides of the line is relatively large. At this time, the CDP has the risk of no-trip failure. For the protection no-trip failure caused by excessive phase difference of the current, the phase difference can be reduced by current phase compensation, so as to improve the protection sensitivity and avoid no-trip failure.

  - Current phase compensation on the energy storage side and its problems

Based on the idea of phase compensation, the phase compensation principle on the energy storage side can be designed as shown in . When the energy storage station is charging, a phase compensation angle is added to the phase of current received by protection installed on the storage side to reduce the phase difference.

In ,  is the compensated phase current of protection 3. Replacing the phase difference  in  with and simplifying,  can be obtained.

In ,  is the ratio of compensated differential momentum and compensated braking momentum.

It should be noted that although 1 is used as the threshold in  and , if  or  is only slightly greater than 1 during a fault, the protection should still be considered to lack sufficient sensitivity and there is a certain risk of no-trip failure. Therefore, 1.2 is used as the threshold to evaluate the sensitivity of the protection criterion, that is,  () means that the protection cannot operate,  () means that the protection can operate but the sensitivity is insufficient, and  () means that the protection sensitivity is sufficient and can trip reliably.

As shown in Figure 4, the  and  curves when  are shown in Figure 4. The black solid line shows what values of  and  would result in  when the compensation angle  is set to be 0. The lower left area corresponds to , and the upper right area corresponds to . The blue solid and dashed lines correspond to the  and  curves for the 60° compensation angle case. Red curves corresponds to the case where the compensation angle equals 70°.

Fig. 4. Protection action boundaries corresponding to different compensation angles

In Figure 4, comparing the three solid lines, it can be seen that after the current phase compensation, the area of the upper right corner of the curve is significantly reduced, which means the sensitivity of protection is effectively improved. In addition, the sensitivity is higher when the compensation angle is larger.

However, this fixed compensation method has limitations. Taking points X and Y in Figure 4 as an example. The dashed line in Figure 4 indicates . When a fault occurs in the lower left area of the dashed line, the protection sensitivity is sufficient. Point X indicates a fault when  and . This is a possible situation that an in-area fault occurs on the transmission line when the energy storage is charging; Point Y indicates a fault when and . This situation may arise due to measurement errors or other reasons when the fault occurs outside the area.

If the compensation angle is set to 60°, then point X is located in the upper right part of the blue dashed line, its  equals to 1.07. At this time, it is close to the boundary of the protection action and does not have sufficient protection sensitivity. If the compensation angle is increased to 70° to improve the protection sensitivity at point X, making point X located in the lower left of the red dashed line. Then point Y is already close to the action boundary, and it cannot be guaranteed that the protection does not operate during external faults. This contradiction between sensitivity and reliability also exists in the methods proposed in [8]-[9]. Therefore, to further improve the performance of current differential protection based on phase compensation, it is necessary to analyze the fault characteristics when the fault occurs near point X or in the upper right corner of point X and Increase the compensation angle  separately at this time.

  - Adaptive phase compensation method considering energy storage control strategy

    - Characteristics of negative sequence current in transmission lines of grid-connected energy storage plant

To solve the above problems, this paper introduces the negative sequence component of short-circuit current to assist in identifying faults in the area near point A or the upper right corner of point A in Figure 4. In the system shown in Figure 2, the grid-side short-circuit current is usually several times the short-circuit current on the storage side. Faults in the area near point A or the upper right corner of point A are only likely to occur when the fault resistance is large or when the line impedance between the fault point and point M is very high.

Taking the asymmetrical fault of line QN as an example, when the fault resistance is large, the positive sequence voltage at the energy storage grid-connection point is usually greater than 0.9 p.u.. Refer to , it can be concluded that the negative sequence current at protection 1, 2, and 3 is 0. Because of the asymmetrical fault, the negative sequence current at protection 4, 5, and 6 is not 0. For faults with small fault resistance, the positive sequence voltage at the energy storage grid-connection point is less than 0.9 p.u. At this time, Refer to , the energy storage absorbs negative sequence reactive current. The negative sequence currents at protection 1, 2, and 3 are not 0, and that at protection 4, 5, and 6 are also not 0. Therefore, only the protection of line QN will show characteristics: when the fault resistance is large, the protection installed closed to the energy storage plant has no negative sequence current, whereas the protection installed closed to the grid has negative sequence current.

    - Adaptive phase compensation method

Based on the negative sequence current characteristics of section A, this paper splits the phase compensation angle on the energy storage side into two sides. Under the premise of detecting that the energy storage is in the charging state, for the protection installed closed to the energy storage side, the large compensation angle  is used to modify the current phase when its negative sequence current is 0, and the small compensation angle  is used to modify the current phase when the negative sequence current is not 0. The selection of large and small compensation angles for the protection installed close to the system side is opposite to that of the protection on the energy storage side. Summarizing the above compensation methods, the adaptive phase compensation principle is obtained as shown in (9) and (10), and the compensation angles for different fault conditions are shown in Table 1.

In  and ,  and  are the compensated phase currents of protection 3 and 4.  is the large compensation angle, and  is the small compensation angle. Their specific values are determined during protection setting.  is the negative sequence current starting value.

TABLE I

Phase compensation angle under different fault conditions

| Asymmetric faulta |  |  |
| --- | --- | --- |
|  | Internal faults | External faults |
|  |  | + |
|  | + | + |
| Symmetrical fault |  |  |
|  | Internal faults | External faults |
| Any | + | + |

From Table 1, it can be seen that if a fault occurs on the line QN and fault resistance is large at this time, then the adaptive compensation methods shown in  and can reduce the current phase difference by , whereas the current phase difference of lines PQ and NM is reduced by +. Through the protection setting, the sensitivity of the CDP can be increased without reducing the reliability of protection during external faults.

If a fault occurs on the line QN, and the fault resistance is small or it is a metallic fault, then , and the current phases difference of lines PQ, QN, and NM are all compensated by +, which is similar to the method analysed in chapter 3 section A. However,  is usually very small at this time. Although the setting value of + needs to be limited to a lower level to ensure protection reliability during external fault, it can still ensure enough protection sensitivity.

  - Modified current differential protection based on adaptive phase compensation

Based on the above adaptive phase compensation method, modified current differential protection criterion based on adaptive phase compensation(MCDP) can be obtained as shown in .

Action logic of the MCDP is shown in Figure 5.

Fig. 5. Action logic of the MCDP

  - Setting method of the MCDP

In the MCDP, , , and needs to be set. Among them,  and  should be set according to the following principles.

    - Protection should not malfunction during external faults

When an external fault occurs, the current phase difference between two sides of the protected line is about 180°, and the current amplitude ratio  is 1. Bring =1 and  into , the differential protection should be reliably inoperative, so there is (12).

Where  is the reliability coefficient, in order to ensure the reliability during external fault, the value should be less than or equal to 0.7. In this paper 0.7 is taken. As  increases, the sensitivity of protection increases, so this article sets the value of  according to the case where the  is equal.

    - Protection should have sufficient sensitivity during internal faults

Equation  has set A to ensure the highest sensitivity under the premise of reliability, and the set principle of compensation angle  should be such that, in the most severe case of an internal fault, protection can still operate reliably. Thus bringing =1 and  into  and taking the equal sign, equation  can be obtained.

In ,  is the reliability coefficient, and its value should be greater than or equal to 1.1, which is taken as 1.1 in this article. When the  of the protection device is determined, the values of  and  can be determined according to  and . Due to the characteristics of differential protection, the setting of  and  is only related to the braking coefficient  and is not affected by the operating mode of the system, the length of the line, or fault type.

For the setting of , it should be ensured that it is higher than the negative sequence current value caused by measurement errors and other reasons under non-fault conditions to ensure the reliability of protection. In this article, it is set at 5% of the rated current of the energy storage plant.

IV. Simulation Verification

Build the simulation model according to the system structure shown in Figure 2, with line parameters and external system equivalent impedance as shown in Table Ⅱ. The lengths of lines PQ, QN, and NM are all 20 km, and the energy storage station capacity is 100 MW.

TABLE Ⅱ

Line parameters and system equivalent impedance

| Line positive sequence impedance | 0.074+j0.42(Ω/km) |
| --- | --- |
| Line zero sequence impedance | 0.222+j1.26(Ω/km) |
| System Equivalent Impedance | 1.39+j7.88(Ω) |

Refer to  and , set  and , assuming the braking coefficient  of the protection device is 0.8, it can  be obtained that  and . the performance of the MCDP under different fault conditions and energy storage capacities are tested by simulation.

  - Performance at different fault resistances

In the simulation, the energy storage is set to work in the charging state, and a single-phase grounded short circuit occurs at the midpoint of the line QN at 1.5 s. The fault resistances are 0 Ω, 35 Ω, 40 Ω, 100 Ω, and 500 Ω, respectively.

The curves of  and  under each fault are shown in Figures 6(a)-(e). The negative sequence component of the short-circuit current on Q side and N side at fault resistances of 35Ω, 40Ω and 500Ω is shown in Figure 7.

Fig. 6. Performance of the MCDP with different fault resistances

As shown in Figure 6, when energy storage is charging, regardless of the fault resistances, the sensitivity of the MCDP is higher than that of the CDP. As the fault resistance increases,  of the CDP encounters a no-trip failure, but  of the MCDP maintains above 1.2, ensuring reliable operation.

Comparing Figure 6(b) and (c), it can be observed that when the fault resistance increases from 35Ω to 40Ω, the steady-state value of  increases. Combining this with figure 7, it can be seen that the increase in sensitivity at this time is due to , where the energy storage does not absorb the negative sequence current, and the compensation angle has switched to .

Fig. 7. Amplitude of negative sequence component of short-circuit current at different fault resistances

It can be seen from Figure 7 that before the compensation angle switched (fault resistance 35Ω), the negative sequence component of the short-circuit current on the energy storage side (Q side) is much greater than 5% of the rated current; when the compensation angle is just switched (fault resistance 40 Ω), the negative sequence component of the short-circuit current on the energy storage side (Q-side) is much smaller than the 5% rated current; when the fault resistance is very large (500Ω), the short-circuit current on the system side (N side) is much greater than 5% of the rated current. Therefore, using 5% of the rated current as a threshold value can ensure reliable identification of the negative sequence component.

  - The impact of fault location on protection performance

Set the energy storage to operate in charging mode during the simulation, and set a phase A ground short circuit at positions F1-F5 at 1.5s, with fault resistance of 100Ω. The positions for F1-F5 are set as follows: F1: 5% from bus Q on line PQ; F2: 5% from bus Q on line QN; F3: 5% from bus N on line QN; F4: 5% from bus N on line NM; F5: 5% from bus M on line NM. The steady-state values corresponding to each fault position are shown in Table Ⅲ.

TABLE Ⅲ

Line parameters and system equivalent impedance

| Position |  | Performance of the MCDP |
| --- | --- | --- |
| F1(out of QN ) | 0.6370 | correct no-action |
| F2(in QN) | 1.2799 | correct action |
| F3(in QN) | 1.3214 | correct action |
| F4(out of QN) | 0.6380 | correct no-action |
| F5(out of QN) | 0.6380 | correct no-action |

It can be seen from Table Ⅲ that regardless of whether the fault occurs inside or outside the area, the MCDP can correctly identify it, and the fault location does not affect the performance of the MCDP.

  - The impact of fault types on protection performance

Set the energy storage to operate in charging mode during the simulation. At 1.5 seconds, different types of faults occur at the midpoint of line QN, with each fault type and corresponding fault resistance shown in Table Ⅳ. The  and  curves of single-phase grounded short circuit in Table 4 are shown in Figure 6(d). The  and  curves for other cases are shown in Figure 8(a)-(e).

TABLE Ⅳ

Fault types and corresponding diagrams

| Fault Type | Fault Resistance | Figure |
| --- | --- | --- |
| AG | 100Ω | Fig6(d) |
| AB | 10Ω | Fig8(a) |
| ABG | 100Ω | Fig8(b) |
| ABC | 0Ω/20Ω/100Ω | Fig8(c)/(d)/(e) |

Fig. 8. Performance of the MCDP under different fault types

When the fault type is an asymmetric fault, it can be seen from Figures 6(d), 8(a), and (b) that  is greater than 1.2, and the MCDP can ensure reliable operation.

When the fault type is a three-phase short circuit, there are fluctuations in  and  in Figure 8(c). This is because the fault is metallic at this time, and the voltage at the energy storage grid connection point is too low to maintain charging state. However, at this time,  is greater than 1.2, and the protection can operate normally. From Figures 8(e) and (f), it can be seen that when the fault resistance of the three-phase short circuit is increased to above 20Ω, the MCDP may have insufficient sensitivity, but it is still better than the CDP.

  - The impact of line length on protection performance

Change the length of line QN in the simulation to 5km, 20km, 40km, and 60km , and a phase A ground short circuit occurs at 1.5s with a fault resistance of 100Ω.  and  for each case are shown in Figure 9(a) and (b), respectively.

Fig. 9. Performance of the MCDP with different line lengths

Comparing Figure 9 (a) and (b), it can be seen that the MCDP consistently ensures  during the variation of the length of line QN, and the differential protection can operate reliably, with sensitivity significantly better than traditional protection.

  - The impact of energy storage capacity on protection performance

In the simulation, the energy storage capacity is set to 50MW, 100MW, and 200MW respectively. A phase A ground fault occurs at the midpoint of line QN at 1.5s, with a fault resistance of 100Ω. and  for each case are shown in Figure 10(a) and (b), respectively.

Fig. 10. Performance of the MCDP with different energy storage capacities

Comparing Figure 10 (a) and (b), it can be seen that when the energy storage capacity increases, the sensitivity of the CDP is obviously insufficient, but the MCDP can still ensure the reliable operation.

  - The impact of synchronization error on protection performance

Analyze the impact of synchronization error on protection performance under extreme conditions (time difference ). At 1.5s, a phase A ground short circuit occurs at the midpoint of line QN, with a fault resistance of 100Ω. The and  curves for protection of lines PQ, QN, and NM under a synchronization error of 0.3ms are shown in Figures 10 (a) - (c).

As shown in Figure 11, under a synchronization error of 0.3ms, the MCDP can still ensure that the protection can correctly identify faults.

Fig. 11. Protection performance under a synchronization error of 0.3ms

V. Conclusion

The modified current differential protection based on adaptive phase compensation proposed in this paper can effectively reduce the risk of current differential protection no-trip failure caused by excessive phase difference of short-circuit current, which usually occurs when a fault occurs in the transmission line during the charging of energy storage stations, and has the following characteristics:

1) In the case of asymmetric faults, the MCDP can ensure reliable operation under different fault locations, line lengths, energy storage capacities, and the presence of synchronization errors. It has ability to resist fault resistance and can improve sensitivity during internal faults without reducing the reliability of external fault protection.

2) In the case of symmetrical faults, the sensitivity of the MCDP is significantly better than that of traditional current differential protection.

References

- Technical specification for connecting wind farm to power system—Part 1: On shore wind power, Standardization Administration of the People's Republic of China GB/T 19963.1-2021, 2021．

- Technical requirements for connecting photovoltaic power station to power system, Standardization Administration of the People's Republic of China GB/T 19964-2024, 2024．

- Technical requirements for power conversion system of electrochemical energy storage system, Standardization Administration of the People's Republic of China GB/T 34120-2023, 2023．

- T. G. Bolandi, H. Seyedi, S. M. Hashemi and P. S. Nezhad, "Impedance-Differential Protection: A New Approach to Transmission-Line Pilot Protection," in IEEE Transactions on Power Delivery, vol. 30, no. 6, pp. 2510-2518, Dec. 2015.

- K. Solak, J. Herlender and J. Iżykowski, "Transmission line impedance-differential protection with improved stabilization for external fault cases," 2018 19th International Scientific Conference on Electric Power Engineering (EPE), Brno, Czech Republic, 2018.

- Y. Guo, Z. Zhou, Y. Liu, et al. New Principle of Line Differential Protection Based on Combined Current and Voltage Restraint Principle. Proceedings of the CSEE, 1-14[2025-01-07].

- K. Jia et al., "Pilot Protection Based on Amplitude Comparison for Renewable Power Teed Lines," in CSEE Journal of Power and Energy Systems, vol. 8, no. 6, pp. 1519-1529, November 2022.

- C. Lan, S. Huang, J. Zhang, J. Meng, H. Zhang and X. Zheng, "A Novel Principle of Current Differential Protection for Renewable Energy Station," 2023 IEEE International Conference on Advanced Power System Automation and Protection (APAP), Xuchang, China, 2023, pp. 519-523.

- L. Zang, G. Zou, C. Zhou, M. Zheng and T. Du, "Ad-axis based current differential protection scheme for an active distribution network," in Protection and Control of Modern Power Systems, vol. 7, no. 2, pp. 1-11, April 2022.

- M. Farshad, "A Pilot Protection Scheme for Transmission Lines of Half-Bridge MMC-HVDC Grids Using Cosine Distance Criterion," in IEEE Transactions on Power Delivery, vol. 36, no. 2, pp. 1089-1096, April 2021.

- A. N. R. L. Sirisha and A. K. Pradhan, "Cosine Similarity Based Directional Comparison Scheme for Subcycle Transmission Line Protection," in IEEE Transactions on Power Delivery, vol. 35, no. 5, pp. 2159-2167, Oct. 2020.

- L. Zheng, K. Jia, T. Bi, Y. Fang and Z. Yang, "Cosine Similarity Based Line Protection for Large-Scale Wind Farms," in IEEE Transactions on Industrial Electronics, vol. 68, no. 7, pp. 5990-5999, July 2021

- Y. Zhang, Y. Li, J. Song, X. Chen, Y. Lu and W. Wang, "Pearson Correlation Coefficient of Current Derivatives based Pilot Protection Scheme for Long-distance LCC-HVDC Transmission Lines," 2019 IEEE 8th International Conference on Advanced Power System Automation and Protection (APAP), Xi'an, China, 2019, pp. 1367-1371.

- L. Chen et al., "Similarity Comparison Based High-Speed Pilot Protection for Transmission Line," in IEEE Transactions on Power Delivery, vol. 33, no. 2, pp. 938-948, April 2018.

- Y. Zhang, Y. Yu, G. Yang, T. Zheng and T. Sun, "Adaptive Current Differential Protection Principle for Transmission Line Connected to Energy Storage Power Station Based on Amplitude and Phase Compensation," 2024 3rd International Conference on Energy and Electrical Power Systems (ICEEPS), Guangzhou, China, 2024, pp. 49-53.

- Y. Liang, Y. Ren and W. He, "An Enhanced Current Differential Protection for AC Transmission Lines Connecting MMC-HVDC Stations," in IEEE Systems Journal, vol. 17, no. 1, pp. 892-903, March 2023.

- K. Jia, C. J. Gu, Z. W. Xuan, L. Li and Y. Q. Lin, "Fault characteristics analysis and line protection design within a large-scale photovoltaic power plant", IEEE Transactions on Smart Grid, vol. 9, no. 5, pp. 4099-4108, Sep. 2018.

- V. Telukunta, J. Pradhan, A. Agrawal, M. Singh and S. G. Srivani, "Protection challenges under bulk penetration of renewable energy resources in power systems: A review", CSEE Journal of Power and Energy Systems, vol. 3, no. 4, pp. 365-379, Dec. 2017.

- L. J. Chen and S. W. Mei, "An integrated control and protection system for photovoltaic microgrids", CSEE Journal of Power and Energy Systems, vol. 1, no. 1, pp. 36-42, Mar. 2015.

Haoyu Zhu received the M.Sc degrees in Electrical Engineering from Shanghai Jiao Tong University, China, in 2019 and then worked as a PhD candidate until now.

His research interests include power system protection, renewable energy and microgrid automation and power system optimal configuration.

Xiaoran Wang graduated from Hohai University in 2022 with a bachelor's degree in Electrical Engineering, and then entered the Department of Electrical Engineering at Shanghai Jiao Tong University to pursue a Master's degree in Electrical Engineering.

His research focuses on Relay Protection in New Energy Access Systems and Grid-connected energy storage technology.

Chunju Fan received the Ph.D. degree from Shanghai Jiao Tong University, China, in 2005.

She is currently an associate professor of Electrical Engineering, Shanghai Jiao Tong University. Her research interests include power system relay protection, power system fault analysis and smart grid.

Yan Hu is currently an associate professor of Electrical Engineering, Shanghai Jiao Tong University. His research interests include smart grid fault analysis, microgrid control and protection, intelligent substations and power system information security.

Nengling Tai received the Ph.D degrees in Department of Power Systems and Automation, Huazhong University of Science and Technology, China, in 2000.

He is currently a distinguished professor of Shanghai Jiao Tong University and serving as deputy dean of the Smart Energy College of Shanghai Jiao Tong University. His research interests include smart grid protection, integrated energy system optimization, ship power system optimization design and ship power system protection technology.

This work was supported by National Natural Science Foundation of China(No. 52337006).

Haoyu Zhu is with the College of Smart Energy, University of Shanghai Jiao Tong (e-mail: zhy119031910026@sjtu.edu.cn ).

Xiaoran Wang is with the Schoool of Electronic Information and Electrical engineering, University of Shanghai Jiao Tong. (e-mail: wxrwljj0301@sjtu.edu.cn ).

Chunju Fan is with the Schoool of Electronic Information and Electrical engineering, University of Shanghai Jiao Tong. (e-mail: fanchunju@sjtu.edu.cn).

Yan Hu is with the Schoool of Electronic Information and Electrical engineering, University of Shanghai Jiao Tong. (e-mail: yanhu@sjtu.edu.cn ).

Nengling Tai is with the College of Smart Energy, University of Shanghai Jiao Tong (e-mail: nltai@sjtu.edu.cn).