Shapelet-based Method for Short-Term Voltage Stability Assessment considering Interaction Mechanisms in Multi-Infeed HVDC System

Yubo Sun1, Shuqing Zhang1, Chao Lu1

- Department of Electrical Engineering, Tsinghua University

Correspondence: Shuqing Zhang (zsq@tsinghua.edu.cn)

Abstract

The short-term voltage stability (STVS) of a multi-infeed high-voltage direct current (MIHVDC) system is controlled by complex dynamic reactive power interactions that have multifactor coupling and strong time-varying characteristics. However, because of the complexity in decoupling these interactions, traditional analytical methods cannot accurately quantify their effects on stability. The STVS analysis of MIHVDC systems involves several challenges, such as high-dimensional, time-varying, and nonlinear characteristics. To address these challenges, this paper proposes an STVS evaluation method based on a multi-time-scale (MTS) interaction mechanism and time-series data mining. First, a multi-timescale interaction mechanism is proposed on the basis of dynamic responses. The short-term voltage instability process can be divided into three stages, namely, power flow transfer, dynamic reactive power regulation, and hierarchical cascade electromechanical interactions. This clarifies the accumulation and propagation mechanisms of reactive power deficiency at different timescales. Second, this paper proposes a time-series data mining method based on shapelets to solve problems in traditional STVS analysis. However, the dynamic response caused by commutation failure of the HVDC system interferes with the accuracy of time-series data mining. To solve this problem, this paper presents the optimization of the method by combining it with the dynamic mechanism and proposes the synchronous cluster of shapelets (SynCShapelet) method. In addition, the physical relationship between the shapelet and critical operating point of the dynamic load is elucidated, thus addressing the black-box problem and low confidence of machine learning methods. As demonstrated via a case study, SynCShapelet can predict the instability of the system by detecting features and incorporating the MTS interaction mechanism to preliminarily assess the path of the short-term voltage instability. In the application scenario of the STVS of MIHVDC, the proposed method provides a theoretical basis and technical support for the STVS evaluation and control strategy.

Keywords: multi-infeed HVDC; dynamic load; STVS; MTS interaction mechanism; time-series data mining;

| Nomenclature |  |  |  |
| --- | --- | --- | --- |
|  | Reactive power of the motor |  | Dynamic direct current |
|  | Motor voltage |  | Equivalent susceptance of the compensation device |
|  | Stator–rotor mutual reactance |  | Dynamic voltage of the converter bus |
|  | Stator resistance |  | No-load voltage of the converter transformer valve side |
|  | Rotor resistance |  |  |
|  | Slip |  | Power factor angle |
|  | Stator leakage reactance |  | Direct voltage |
|  | Rotor leakage reactance |  | Direct current |
|  | Motor inertia time constant |  | Initial reactive power balance point of the AC system |
|  | Mechanical torque |  | Short-circuit capacity of the converter bus |
|  | Electromagnetic torque |  | Time constant of the AC system |
|  | Manifold curvature |  | Critical slip |
|  | Dynamic reactive power of the converter station |  | Slip corresponding to the critical fault clearing time |
|  |  |  | Shapelet feature |
|  | Reactive power consumption of the converter station |  | Metric function |
|  |  |  | Occurrence time of the shapelet feature |
|  | Dynamic output of the reactive power compensation device |  | Time series |
|  |  |  | Set of candidate subsequences |
|  | Dynamic direct voltage |  | Extinguishing angle |
|  | Number of bridges per pole |  | Firing angle |
|  | Transformer turns ratio of the converter transformer |  | Equivalent commutation reactance |

- | Introduction

Recent years have seen a rapid development of ultra-high voltage direct current (UHVDC) transmission projects worldwide. Typical projects include the 1,050 kV experimental project in Italy [1, 2], the UHVDC system in China [3, 4], and the ±800 kV high-voltage direct current (HVDC) system jointly designed by India and Germany [5]. These technologies have significantly improved the economics and stability of power transmission [6, 7]. However, with the development of multi-infeed HVDC (MIHVDC) systems, short-term voltage stability (STVS) has attracted considerable attention. In MIHVDC systems, the power flows can undergo substantial shifts under heavy disturbances, triggering rapid responses from the dynamic components. MIHVDC systems usually have structural issues, such as high load density, concentrated DC feed locations, and insufficient dynamic reactive power support at load centers, resulting in a serious imbalance between the reactive power supply and demand. Currently, major power grids worldwide have the characteristics of robust structure, abundant capacity, and wide-area interconnection. The issues of power angle and frequency stabilities are no longer prominent in MIHVDC systems. Consequently, the STVS in MIHVDC scenarios has become a key constraint on grid security. Therefore, the dynamic mechanism of STVS under multifactor coupling warrants extensive research.

The STVS in MIHVDC systems has become an important research focus. Previous studies have primarily employed time-domain simulations [8] and analytical methods based on transient energy functions [9]. Detailed mathematical models can accurately capture the dynamic characteristics of the components in large-scale systems; however, their computational demands are too intensive for real-time applications. Although energy-function methods are faster, they are ineffective in addressing the complexity of modern power systems. The high dimensionality, time variation, and nonlinearity of the problem complicate rapid and accurate analytical evaluations.

Recently, with the application of data mining and phasor measurement unit (PMU) measurements, data-driven machine learning algorithms have been proven to be capable of performing predictive assessments of STVS. Traditional machine learning algorithms, such as artificial neural networks (ANN) [10], support vector machines (SVM) [11, 12], decision trees (DT)[13, 14], random forests (RF)[15], XGBoost [16], and extreme learning machines [17], play a significant role in addressing traditional STVS challenges in complex power systems. Traditional machine learning algorithms have the advantages of strong interpretability, close integration with physical mechanisms, and high recognition of explicit features.

However, deep-learning methods offer automatic feature extraction by processing raw data through multiple hidden layers. Current deep-learning models [18] used in the short-term stability assessment of power systems include convolutional neural networks (CNNs) [19, 20], deep belief networks (DBNs) [21, 22], and long short-term memory networks (LSTMs) [23]. Although deep-learning models are suitable for large-scale power systems, they have limitations pertaining to the mechanism, interpretability of results, visualization and identification of features, and continuity of results. These limitations are critical disadvantages for power system analyses, particularly for STVS assessment.

Moreover, the theoretical system for STVS for MIHVDC systems remains incomplete. Given their interpretability, deep learning models cannot ensure validity. Algorithms that are closely integrated with physical mechanisms and based on machine learning models are more appropriate for the current challenges. This paper presents an evaluation framework that shows significant advantages in terms of key performance as compared with existing methods. Traditional time-domain simulations and energy function methods make it difficult to quantify high-dimensional, nonlinear, and dynamic reactive power interactions. Machine-learning models are limited by static feature extraction, whereas deep-learning models can handle time-series data but lack physical explicability. In the proposed framework, the complex dynamic process is decomposed into three identifiable stages through a multi-timescale (MTS) interaction mechanism. A multi-dimensional synchronous shapelet-based approach, referred to as synchronous cluster of shapelets (SynCShapelet), is proposed for extracting features related to transient voltage instability. A coupled modeling of multi-dimensional temporal features and dynamic mechanisms is achieved by utilizing the SynCShapelet algorithm, thus overcoming the sensitivity of traditional methods to commutation failure interference. The "black box" problem associated with machine learning models was also addressed through the physical correlation between the trajectory bifurcation feature and critical slip.

The remainder of this paper is organized as follows. Section 2 presents an analysis of the MTS interaction mechanisms of the STVS factors within the MIHVDC system. This description emphasizes how dynamic reactive power characteristics can influence feature extraction for the STVS. Section 3 presents SynCShapelet; this approach effectively addresses the challenges posed by the rapid response characteristics of DC systems for STVS assessment in MIHVDC systems. The mechanistic analysis that substantiates the validity of SynCShapelet in extracting instability features is also detailed. Section 4 presents a case study that validates the efficacy of the proposed shapelet-based methodology, which considers AC/DC MTS interactions, for evaluating the STVS in MIHVDC systems. Finally, Section 5 summarizes the principal conclusions drawn from this study and provides recommendations for future research.

- | MTS Interaction Mechanism for STVS in MIHVDC system

To effectively mine time-series data features for STVS assessment, it is crucial to understand the interaction mechanisms and identify distinct modes within the transient process. This section discusses the key factors of the STVS. The timescales of the transient voltage interaction processes are divided by quantitatively analyzing the reactive power dynamics of these factors. The MTS interaction mechanism was summarized to elucidate the evolution path of the transient voltage interaction in the MIHVDC system.

2.1 | Key Factors of STVS

The essence of the STVS lies in the balance of dynamic reactive power [24]. The main process of STVS within an MIHVDC system involves the transient balance of reactive power among the HVDC system, composite loads, traditional power supply systems, and reactive power compensation equipment. This study focused on dominant instability processes as an entry point to analyze the primary factors influencing the STVS.

Factors affecting the STVS in MIHVDC systems can be categorized into four groups: 1) HVDC System Factors: Inverter commutation failures, reactive power absorption, control modes, and shunt reactive compensation. 2) Composite Load Center Factors: Instability associated with local and remote induction motors in low-voltage areas. 3) Traditional Power Source System Factors: Subtransient processes, dynamics of excitation regulation, and rotor mechanical responses. 4) Dynamic Reactive Power Compensation Devices: Primarily including synchronous condensers, static reactive power generators (SVGs) [25], and static reactive power compensators (SVCs) [26]. In contemporary MIHVDC systems, the influence of traditional power sources on the STVS is relatively weak because of the gradual elimination of high-energy-consuming units and large electrical distances. Reactive power compensation predominantly relies on filtering devices at inverter stations, whereas high-cost HVDC dynamic reactive power compensation remains a challenge for wide implementation. Consequently, this study primarily investigated the impact of dynamic variations in reactive power within HVDC systems and composite loads, along with their interactions across the MTS on the STVS.

2.2 | Distinguishable MTS Interaction Mechanism

(1) MTS of dynamic reactive power interaction

Through analyses and studies of commutation failure under LCC-HVDC, the multilevel response mechanism of the HVDC control system, and the dynamic characteristics of composite loads, it was concluded that the response timescales of the different devices after the disturbance were diverse in the MIHVDC system, and there were three distinct response timescales. According to the response times from fast to slow time scales are divided into less than 10 ms, 10 ms to less than 1 s, and 1 s to 10 s, as shown in FIGURE 1.

(2) Analysis of interaction processes across different timescales

The dynamic reactive power factors across various response time scales were distributed and interacted with each other through the network when faults occurred in the MIHVDC system. Therefore, an MTS interaction occurred during the transient voltage instability of the MIHVDC system. The MTS interaction process associated with the STVS can be categorized into three distinct stages, as illustrated in FIGURE 2.

In the millisecond-level process, namely, electrical circuit interaction, significant disturbances cause commutation failure of converter valves, DC voltage distortions, current surges, and hysteresis of dynamic reactive power compensation. Such disturbances may result in an imbalance in reactive power, thereby increasing the risk of voltage instability at adjacent stations. In the process of tens to hundreds of milliseconds level, namely, the control of dynamic reactive power sources and loads, voltage distortion triggers a rapid response from HVDC inverter buses, whereas the instability of high-proportion dynamic loads leads to a sharp increase in reactive power demand, which causes the formation of local low-voltage regions. In the second-level process, namely, the machine-network interaction process of hierarchical dynamic loads, motor instability in low-voltage regions leads to a surge in reactive power demand and difficulty in voltage recovery. The voltage distortion further leads to the cascading instability of adjacent motors, which eventually causes voltage collapse in the low-voltage area, spreads to the main grid, and even leads to system-level collapse. The interaction process reveals three distinct instability modes for the short-term voltage instability of the MIHVDC system. These modes reflect the different dominant roles of HVDC systems and dynamic loads, providing a theoretical basis for using feature-mining methods to distinguish instability patterns.

FIGURE 1 | Dynamic response time scales of STVS factors in MIHVDC system.

FIGURE 2 | Dynamic reactive power interaction across time scales in MIHVDC system.

2.3 | Dynamic Reactive Power Quantification of STVS Factors

Based on the physical processes inherent in HVDC systems and composite loads, this section delineates the time-varying characteristics within the STVS of an MIHVDC system. The analysis focuses on two primary factors: 1) the influence of voltage distortion on extinction angles during disturbances in LCC-HVDC systems, including commutation failures, inverter lockouts, and the dynamic reactive power characteristics of HVDC inverters following a commutation failure, and 2) the dynamics of reactive power affected by the coupling of composite loads with high penetration of motors, as well as hierarchical motors within the Q-V process of AC systems. Special emphasis is placed on how these dynamic factors interact across various timescales and subsequently affect the reactive power dynamics.

The STVS of MIHVDC fundamentally represents the STVS of the load terminal voltage on the AC side. The dynamic behavior associated with the predominant instability is primarily influenced by reactive power demand variations from the motors and the HVDC system.

From a differential geometry perspective, transient voltage trajectories form unique curve features during dynamic processes in the phase space. However, because of the structural complexity inherent in MIHVDC systems, analyzing this special trajectory using traditional methods is challenging. Nevertheless, shapelet-based data-mining methods aim to identify subtrajectories with unique manifold curvatures.

where and  are the first- and second-order characteristics of the motors and HVDC system, respectively. Similarly, during system dynamics, the "sub-trajectories with unique manifold curvature" formed by voltage and active power in phase space are also targets of data mining.

(1) Analytical Expression of Dynamic Characteristics in Motors

In an MIHVDC system, the instability of the induction motors predominates over that of the STVS at composite load buses. The dynamic changes in reactive power within the motors are intricately linked to the transient voltage trajectories. Owing to the inherent dynamic characteristics of these motors, both active and reactive powers exhibit subtrajectories characterized by unique manifold curvatures during periods of instability, which are marked by significant variations in their first and second derivatives.

FIGURE 3 | Equivalent circuit diagram of an induction motor.

Using the classical third-order induction motor model, the reactive power equation can be expressed as

Differentiating equation  concerning time yields:

Where the slip dynamics equation is:

The second derivative of reactive power from equation  is:

The second derivative of slip is obtained from the slip dynamics equation:

where the terminal voltage change rate is determined by the contingency response time constant (system inertia),  reflects the dynamic characteristics of the motors, and the slip change rateis determined by the inertia of the motors and the difference between the mechanical and electrical torques.

In MIHVDC, Shapelet mining of the STVS on the AC side is equivalent to finding the special trajectories of the first- and second-order characteristics of the motors, which considers the sufficient dynamic factors of the STVS. (A specific description of these special curve changes is presented in this case study.) Moreover, special trajectories may also be infected by HVDC system controls.

(2) Analytical Expression of Commutation Failure Recovery in HVDC Systems

After fault clearance, the commutation failure recovery process dominates over the STVS at the terminal buses of the HVDC inverter station. The first and second derivatives of the dynamic response data can be used to analyze instantaneous reactive power changes during commutation failure recovery, providing a quantitative basis for STVS analysis. The relevant expressions are as follows:

The dynamic reactive power consumption equation for converter stations was improved through a quasi-steady-state analysis of the dynamic reactive power model:

The dynamic modification expressions for and  are based on the dynamic analysis of the HVDC system in [27].

Using the multiplication and chain rules for differentiation, the first derivative (dynamic reactive power change rate) and second derivative (dynamic reactive power acceleration) of the composite function for the dynamic reactive power  are derived as follows:

Expanding equation (9) completely using multiplication and chain rules for differentiation yields:

where the DC voltage change rate  is determined by the DC control system (e.g., constant current control); the DC change rate  is influenced by the voltage-dependent current limit (VDCOL); the power factor angle change rate  is related to the recovery rate of the converter bus voltage;  and  reflect the acceleration responses of the DC control system;  is caused by nonlinear changes during converter bus voltage recovery; and  reflects the strong coupling between reactive power and voltage, directly related to the short-circuit ratio (SCR).

Using V-Q sensitivity analysis based on the short-circuit capacityand combining the transient reactive power imbalance, the equation of the time-domain voltage responses is derived as

The typical time constant  for an AC system was 100-500 ms [28]. Furthermore, a lower SCR resulted in a reduced time constant. As discussed in Section 2.2, within the time frame of 10 to several hundred ms, a dynamic reactive power interaction occurs between the motor transient and commutation failure recovery processes. Because of the similarities between the first and second derivatives of these processes, the veracity of the shapelet-based algorithm may be affected.

- | Shapelet-based STVS Feature Extraction and Classification

It is precisely because STVS shows complex dynamic characteristics at different time scales, which is difficult to be captured by traditional methods. Therefore, we introduce Shapelet method, which has advantages in discovering local key features in time series data. This section presents the shapelet-based feature extraction algorithm aimed at capturing the key characteristics of transient voltage instability by analyzing the transient response data of the system. Considering the influence of transient interactions in MIHVDC systems, this study proposes enhancements to the algorithm to improve its accuracy. The validity of these improvements was assessed by examining their correlations with the underlying physical mechanisms.

3.1 | Principle of Shapelet

Shapelets are local subseries that can distinguish categories in a time series. Its discriminative ability can be achieved by calculating the minimum Euclidean distance between the target sequence and shapelet. Specifically, given a time series T, the shapelet is defined as a continuous subsequence S within T. The appropriate length of shapelets L is selected by the algorithm. The minimum Euclidean distance between S and all possible subsequences of the target series is calculated as follows.

where  is a set of subsequences of the same length as S in T. This minimum Euclidean distance reflects the local similarity between the target sequence and the shapelet. The smaller the distance, the more likely it is that the sequence belongs to the category corresponding to the shapelet. The quality of a shapelet is evaluated through metric functions such as information gain and binary evaluation. Information gain is achieved by measuring the degree of entropy reduction after the shapelet split the dataset, and the shapelet with the highest information gain is selected as the optimal shapelet.

During the feature transformation process, the original time series is mapped into feature vectors composed of multiple shapelet distances to form shapelet-transformed data. For example, for a set containing k shapelets, each time series can be transformed into a k-dimensional feature vector, where each dimension represents the minimum Euclidean distance between the sequence and corresponding shapelet. Once all k-dimensional shapelets have been determined, the distance between the original time series and the optimal shapelet can be determined. The above conversion process is a shapelet transform that converts the original time-series sequence into flat numerical distance data.

3.2 | Effectiveness Analysis of Shapelet-based Algorithm for STVS

(1) Sufficiency and Necessity Analysis of Transient Voltage Trajectories Based on Motor Dynamic Characteristics

The shapelet-based feature mining algorithm of the STVS is equivalent to identifying the unique curve features of transient voltage trajectories. STVS information should be included in the system trajectories near the critical instability point. Sufficiency and necessity analyses of traditional STVS evaluations are based on the physical characteristics of the motors. The actual critical unstable point lies between the results of the optimistic and conservative estimations.

Based on the state-estimation equivalent method, the dynamic characteristic curves corresponding to the generalized motor model with target loads during and after the fault were derived, as shown in FIGURE 4. The intersection points of the electromagnetic power curves before and after the fault were  and , respectively.  is an unstable equilibrium point, and the corresponding slip value is the critical slip. If the slip exceeds the critical slip, the motor speed cannot recover after the disturbance, which ultimately leads to system instability. The critical slip value was derived as follows:

The analysis revealed that the critical slip criterion based on the prefault steady-state voltage assumption is optimistic because it neglects the delayed voltage recovery effect at the bus after fault clearance. Although the slip upper-bound criterion based on the pre-steady-state voltage does not fully account for the dynamic voltage attenuation, it is considered a sufficient criterion for instability because its threshold occurs later than the actual critical point of instability.

For a conservative estimation, the motors are most likely to lose stability when a three-phase short-circuit grounding fault occurs near the bus. Therefore, the critical clearing time (CCT) of the expected fault can be used as an evaluation index for STVS. During the fault, the electromagnetic power supplied by the system to the load is nearly zero.

FIGURE 4 | Output characteristic curves of the motor model.

In the analysis of the fault critical clearance time, it was assumed that the terminal voltage of the load machine could recover to the level before the fault without losing the load stability, and the change in the load bus voltage during the fault process was ignored. A conservative estimate of the CCT can be obtained by linearizing the slip change rate to the rate corresponding to the . The expression for the slip , corresponding to the CCT, is

The actual instability critical point of the transient process should be between  and , and the unique characteristics of the first- and second-order derivatives in the STVS should also appear in this segment.

(2) Correlation Analysis of Shapelet Features and Instability Mechanisms

The correlation between the shapelet feature and physical instability mechanism is the criterion for judging the validity of the shapelet-based algorithm. In the transient process, motors may experience a critical slip, leading to an unstable state from which system recovery is not possible. During this phase, significant changes occur in the trends of bus voltage as well as active and reactive power. These alterations can be captured effectively using shapelet-based algorithms.

To analyze its effectiveness, it is necessary to further study the correlation between the shapelet characteristics and the physical mechanism of instability. Usually, the length of shapelets is selected by training. To focus on the key points of the mechanism analysis and ensure a clear presentation, the study take length of 50 ms as an example. One hundred cases without DC system interference were selected to construct the training set, the numbers of stable and unstable samples are 58 and 42 separately, and an optimal shapelet with length of 50 ms was extracted through training. The optimal shapelet is represented by black lines in FIGURE 5, and some instability features extracted from other time-series data are represented by red lines.

| （a）Shapelet candidates of P-Scf |  | （b）Shapelet candidates of P-Swj |  |
| --- | --- | --- | --- |
| （c）Shapelet candidates of Q-Scf |  | （d）Shapelet candidates of U-Swj |  |
| FIGURE 5 ¦ Commonality analysis of instability feature time-series segments. |  |  |  |

Through the analysis of the morphological characteristics of the feature fragments, it can be observed that 1) active power instability characteristics: All the feature amplitudes are smaller than the base values, and there is a significant drop, which conforms to the voltage distortion of load nodes and the mechanism of dynamic load instability deceleration in the process of transient voltage instability. 2) Reactive power instability characteristics: All characteristic amplitudes are greater than the base values, and there is an upward trend, which conforms to the mechanism of the dynamic load reactive power surge of load nodes in the process of transient voltage instability. 3) Positive-sequence voltage instability characteristics: All characteristic amplitudes are smaller than the base values, while the voltage amplitude decline rate decreases, showing a concave curve shape, which conforms to the instability mechanism of the dynamic load.

Importantly, in the MIHVDC system, the disturbance caused by commutation failure may affect the instability judgment. The effects of commutation failures can be divided into two categories. However, if the duration of a fault exceeds the critical fault clearance time of the motor, time-domain coupling will exist between the commutation failure recovery process and instability characteristics of the dynamic load after the fault. However, the voltage power response data influenced by the motor do not exhibit distinctive curve characteristics, owing to the monotonicity of the motor speed variation. Instead, during this period, rapid and dynamic fluctuations in voltage and reactive power resulting from both commutation failures and recovery processes in DC converters mimic the curve feature fragments, similar to the critical instability curve characteristics. These imitations do not influence the evaluation of system instability.

However, when the delay in voltage recovery leads to continuous commutation failure, the motor exhibits distinct curve characteristics as it traverses the unstable critical point during this transitional process. However, periodic disturbances arising from continuous commutation failures can cause the voltage curve to repeatedly display quasi-critical instability. This phenomenon directly impacts shapelet-based assessments and results in features discovered by the shapelet-based algorithm being irrelevant to system instability.

The UPQ curve change owing to commutation failure is caused by the fast response controlled by the DC system and simulates the first and second derivative characteristics of transient voltage instability rather than the special curve characteristics formed by the motor crossing the critical point, as shown in FIGURE 6. Therefore, the power variations do not reflect the variation in the system operation point caused by the motor. Therefore, during this period the powers do not present the unique curve characteristic of instability. Combined with the response timescale and power transfer mechanism of the network, these phenomena can be effectively distinguished by a combination of synchronous multi-dimensional features.

| (a) Scf-U | (b) Scf-P | (c) Scf-Q |
| --- | --- | --- |
| FIGURE 6 ¦ Trend of SWJ 525 UPQ feature-segment change interfered by HVDC system. |  |  |

Therefore, this study proposed the use of the difference in the response timescale for screening. By using UPQ combined with Euclidean distance measurement synchronously for STVS classification learning, the interference of the HVDC system in feature mining can be avoided.

3.3 | Synchronous Cluster of Shapelet (SynCShapelet) Classification Algorithm

Based on the MTS interaction mechanism analysis, it was found that the transient voltage trajectory formed special curve characteristics in the phase space, as well as the active and reactive power trajectories, which corresponded to the process of crossing the critical operation point of dynamic load instability.

The conclusion of the second section of this study shows that voltage distortion in the transient process and voltage distortion caused by DC commutation failure usually exist simultaneously in the weak area of a power network with dense HVDC feed points and heavy loads. In this study, the SynCShapelet-based algorithm was used to convert the similarity between the transient response data of the power system state into a group of distance feature measures, and a time-series data classification algorithm based on SynCShapelet was introduced for further training.

First, the candidate subsequence set S was extracted from 3n numbers of transient response time series by sliding window to form L=M-l+1 subsequence. The combinatorial minimum Euclidean distance criterion, GDist, was used to calculate the optimal matching distance between the candidate subsequence combination and the original sequence combination, and the distance dataset  was constructed as follows:

The segmentation strategy was determined by the optimal segmentation point, and the degree of differentiation of candidate subsequences between the two types of labels (stable/unstable) was quantified by introducing the information gain rate as a metric of the classification ability. Finally, shapelet candidate subsequences with optimal classification ability were screened based on the metric function Γ(GDistk). The result is an optimal shapelet with the largest information gain, as shown in equation (16).

Among them, Shpk should obtain the optimal shapelet selected when the metric function value is maximized by an exhaustive search for each candidate subsequence between the minimum and maximum lengths.

3.4 | Classification method based on SynCShapelet

The decision tree model is a hierarchical and structured combination of a series of if-then rules. During its construction process, starting from the root node, the best feature attributes and splitting points (splitting thresholds) are sought at each node such that in the binary branches generated downward from this node, the corresponding sample subsets contain as many similar samples as possible and as few heterogeneous samples as possible. That is, the purity of the sample subset should be as high as possible. The dataset was recursively optimally segmented downward until the number of samples of the same type or sample subsets in the sample subset reached a preset threshold. At this point, tree growth stops. The labels of samples of the same type or samples with a majority advantage in the corresponding sample subset were stored as classification labels in the end-leaf nodes. All branches, internal nodes, and leaf nodes were integrated downward from the root node into a decision tree.

Essentially, the decision tree model obtained through the classification learning of transient time-series datasets is the system's transient voltage stability evaluation model, and a series of tree-like forked if-then rules in the model automatically constitute a combined transient voltage stability criterion. The process of constructing a decision tree (DT) model is a "supervised learning" problem. In this study, a DT was constructed using historical data of the transient process and shapelet characteristics of the simulation results through a systematic method of recursive binary partitioning. The sample space was partitioned by posing continuous questions with yes or no answers.

The basic task of constructing a DT is to repeatedly search for shapelet features of different dimensions and matching distance thresholds on one node, and then branch to another node. The process of identifying attributes for testing and branching is called splitting. The purpose of splitting is to reduce the number of heterogeneous samples in the dataset in the next stage, which can be achieved by calculating the information gain. The calculations were performed in two stages. First, the entropy of the dataset was calculated using the following formula: ; Second, the expected information gain was calculated using entropy: .

- | Case study

The power grid in the case study, characterized as a typical MIHVDC system with significant composite loads, is particularly susceptible to transient voltage instability risks. Given the high time costs and uneven distribution of the original PMU data, this study utilized a model of a real power grid and conducted a simulation analysis based on electromechanical transient simulations using PSD-BPA. A simulation model was developed, and its accuracy and reliability were validated through industrial applications.

The total installed capacity of the power grid was 600.35 GW. The region’s load mainly comprised industrial and commercial sectors, wherein dynamic load forms, such as air-conditioning systems and industrial motors, constitute a substantial proportion of the overall electricity consumption. To accurately reproduce the real-time response data, simulations were conducted using a full-network model with 761 nodes. However, transient voltage stability issues are local problems. Therefore, the focus is on monitoring buses in weak areas.

There are relatively weak and unstable regions in the power grid, namely Scf and Swj. A geographical wiring diagram of the lower-voltage levels in this region is shown in FIGURE 7.

FIGURE 7 | Single-line diagrams of the Scf and Swj areas.

4.1 | Validation and Analysis of MTS Interactions

The MTS mechanism categorizes the transient voltage interactions in MIHVDC systems into three distinct stages according to the time scale. Because of the dynamic elements involved at different stages are diverse, the system power flows exhibit distinct dynamic patterns. These patterns are elucidated via theoretical analyses, quantification of the dynamic processes, and simulation.

In this study, the simulation results of the power grid on the PSA-BPA simulation platform were adopted. This example sets up specific dynamic load configurations. Swj and Scf are connected to three 230 kV nodes, and each 230 kV node is connected to three 115 kV nodes. A schematic of the line connection is shown in FIGURE 7. In this case, a three-phase metallic short circuit occurred near the converter bus at 2 s, and the fault was cleared at 2.1 s. According to the simulation results, it can be observed that the two HVDC systems experienced commutation failure successively during the fault at 2 s and recovered at 2.05 s. The distance between the fault and the weak area near Swj and Scf is approximately 100 km.

| (a) t=2s | (b) t=2.1s | (c) t=5.4s |
| --- | --- | --- |
| FIGURE 8 ¦ Visualization of contour animation for transient voltage variations in the power system. |  |  |

FIGURE 9 | Voltage curves of weak areas with particular monitoring.

FIGURE 8 shows voltage visualizations from 2 to 5.4 s. The instantaneous voltage drops when a fault occurs caused the commutation failure of the two HVDC lines near the fault. The instantaneous effects of fault, commutation failure, and recovery on the STVS of the MIHVDC system proved the existence of an electrical circuit interaction process within 10 ms. The voltage visualization results from 2.1 to 5.4 s show that the system voltage generally recovers to more than 0.85 pu through the interactive process of reactive power dynamic regulation after fault recovery. However, owing to the development of voltage instability in the weak area, the voltage in fault area decreased. This leads to more serious HVDC commutation failures, which eventually develop into more severe transient voltage instabilities.

According to the BPA data and voltage curve of the weak areas in FIGURE 9, after 3 s of fault clearance, the low-voltage motors in the weak area became successively unstable. The increasing reactive power demand further lowers the voltage of the main power grid. This process was caused by the dynamic load instability of the lower-voltage area of the weak region, which then developed into a high-voltage system, finally leading to more serious transient voltage instability. This is the transient interaction process of the hierarchical dynamic load network, which proves the existence of an MTS interaction process.

4.3 | SynCShapelet Feature Extraction and Mechanism Correlation Analysis

The mechanism of STVS can be partially revealed by mining the shapelet characteristics of the instability. However, this method cannot fully determine the correspondence between the SynCShapelet feature and critical instability disequilibrium segment of the operating point in the mechanism analysis. This section analyzes the instability features obtained by the SynCShapelet algorithm, traces the load response curve in the time segment, analyzes the relationship between the instability features and critical period of dynamic load instability, and verifies the reliability of the SynCShapelet algorithm in the STVS assessment. Therefore, the main research goal of this section is to analyze the correlation between data mining methods and the instability mechanism and to reveal the correlation between the feature-appearance period and the period of dynamic loads crossing the critical slip.

Based on the mechanism analysis and the study of the dynamic load participating in the stratified transient interaction process, it is shown that the transient instability of motors in the MIHVDC system presents a phenomenon of successive stalling owing to the diversity of composite loads, where reactive power loss has an "amplification" effect. To calculate the critical slip period of the motor, the results of an arbitrary case selected from the batch samples are analyzed in TABLE 1.

| TABLE 1 ¦ Typical parameters of instability critical points for motors at various voltage levels. |  |  |
| --- | --- | --- |
| Motor | Critical Slip () | Slip at Fault Clearance Time () |
| Swj11 | 0.05816 | 0.04400 |
| Swj 21 | 0.06508 | 0.04345 |
| Swj 525 | 0.07070 | 0.04430 |

The critical slip  can be calculated by the Thevenin equivalent circuit using optimistic torque characteristics. The fault clearance critical slip , which is conservative, was estimated by linearization. The actual critical slip was accurately determined from the real-time measurements of the motor bus voltage, slip, active power, and mechanical power, indicating the precise moment of motor instability. The actual critical slip value should lie between  and .

| (a) Swj corresponding feature time series. | (b) Swj slip corresponding feature time series. |
| --- | --- |
| FIGURE 10 ¦ Swj regional time-series features from an arbitrary case. |  |

As shown in FIGURE 10 (a), the feature extracted from an arbitrary case corresponding to Swj was 2.12-2.17 s. As observed from FIGURE 10 (b), 115, 230 and 525 kV motors in Swj were near the unstable equilibrium point during 2.12~2.17 s. Among them, the slip of a few 115 kV motors is greater than the critical slip, and gradually lose stability. The simulation results show a significant correlation between the time when the instability features appear and the time when the dynamic load crosses the critical slip.

As mentioned previously, the physical processes corresponding to the time series of the instability characteristics of Swj in other arbitrary cases are summarized in FIGURE 11. In FIGURE 11 (b), the 115 kV motors of Swj11, 12 and 13 had become unstable, and the motors of Swj16 had just crossed the unstable equilibrium point and gradually became unstable during the characteristic time series (2.71~2.76s); Swj18 motor is crossing the unstable equilibrium point, Swj14, 15, 17, 19, 21 motor slip is increasing and near the critical slip, about to cross the unstable equilibrium point; Swj22, 23, 525 motor slip is less than the maximum torque slip, the motor is stable. The second batch of motors crossed the unstable equilibrium point after the first batch of motors during the selected feature sequence. At this time, the overall active power reduction at the Swj bus begins to accelerate. In FIGURE 11 (d), during the Swj feature time series (2.15~2.20s), the slips of Swj 15, 21, 22, 23, and 525 motors are less than the critical slip, and the motors are stable, and the slips of Swj 15 and 21 motors are close to the critical slip. The remaining motor slips are near the critical slip and gradually traverse the unstable equilibrium point.

| (a) Swj corresponding feature time series. | (b) Swj slip corresponding feature time series. |
| --- | --- |
| (c) Swj corresponding feature time series. | (d) Swj slip corresponding feature time series. |
| FIGURE 11 ¦ Multi-dimension time-series features in the Swj. |  |

The data suggest that, across all dimensions, the onset of instability features coincides with the dynamic loads near or crossing the critical instability point. Therefore, a correlation exists between the emergence period of the SynCShapelet and the timeframe during which the dynamic loads traverse the critical slip.

4.2 | Results Analysis of SynCShapelet Algorithm

This study adopted the random batch simulation results of the main transmission system of the power grid on the PSA-BPA simulation platform instead of the PMU collection to collect historical transient response data samples.

The study collected the transient response data of the bus state quantity (U/P/Q) within 1 s after the fault for two key observation buses in the weak area, Scf and Swj. The simulation step of the PSA-BPA simulation platform was 10 ms, hence, the step size was set to 10 ms during sample collection to ensure data continuity as much as possible.

In the actual scenario, the load demand exhibited evident diversity. To ensure the accuracy of the STVS assessment, the training dataset considers the diversity of the system power flow distribution over the entire time scale. In this study, three typical operating modes were designed under different power flow operating modes. Various operating modes were realized using the total load power and different dynamic load ratios of Scf and Swj. Specifically, the total load in Swj was 3,250 WM, the total load in Scf was 2,732 MW, and their dynamic loads accounted for 95%, 80%, and 65%. The load distribution diagrams with different voltage levels in Scf and Swj are shown in FIGURE 7.

To demonstrate the transient voltage process of the system under a preset power flow distribution, this case selected the representative N-1 and N-2 accidents of the expected fault set from the calculation file of the system operating mode and recorded the relevant data for a specific period. The fault removal time was uniformly set to 0.1 s. In this study, 1,278 transient cases (534 stable and 744 unstable cases) were randomly generated by the BPA batch simulation platform as the training dataset of the stability judgment model, and 639 cases (320 stable and 319 unstable cases) were used as the test dataset of the stability judgment model. Each case was labeled as stable or unstable based on the simulation results after 10 s.

Through the shapelet transformation of time-series data, stability determination training was conducted to obtain the single-dimensional shapelet feature and classification threshold of the voltage, active power, and reactive power in the Scf and Swj areas. The information gain obtained by the shapelet classification of the single-dimensional transient response data is listed in TABLE 2.

| TABLE 2 ¦ Results of shapelet algorithm in selected single dimensions and SynCShapelet. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Data Dimension | Information Gain (IG) | False judgment rate | Missed judgment rate | Total Accuracy |  |  |  |
| Swj Voltage | 0.6682 | 5.866% | 4.846% | 94.53% |  |  |  |
| Swj Active Power | 0.7172 | 3.073% | 5.727% | 95.90% |  |  |  |
| Swj Reactive Power | 0.7230 | 4.190% | 3.965% | 95.90% |  |  |  |
| Swj SynCShapelet | 0.7444 | 4.460% | 1.010% | 96.88% |  |  |  |

A DT model was constructed, where the internal nodes represent the primary features and classification distance thresholds associated with stable or unstable conditions. A DT can be built based on SynCShapelet and the split thresholds obtained from the bus data dimensions. A DT was built with the root node as the starting point, and the optimal feature dimensions and split points were selected. The resulting bifurcation maximizes the concentration of the same sample while reducing the purity of different samples. Finally, the change in the information gain of the DT classification results was used as the standard to decide whether to stop building a new DT. The DT model construction and split threshold for each node are shown in FIGURE 12.

FIGURE 12 | Multidimensional shapelet DT model diagram.

To verify the applicability of the proposed DT, a set of test samples, including 639 cases, was established to test the accuracy of the DT model classification. The accuracy of the model obtained through the confusion matrix in TABLE 3 was as follows: Accu = (NTH+NTV)/(NH+NV) = 97.03%.

| TABLE 3 ¦ Calculation principle of the confusion matrix. |  |  |
| --- | --- | --- |
| Confusion Matrix | Horizontal Interaction (Actual) | Vertical Interaction (Actual) |
| Horizontal Interaction (Predicted) | NTH（True Horizontal） | NFH（False Horizontal） |
| Vertical Interaction (Predicted) | NFV（False Vertical） | NTV（True Vertical） |
| Total | NH | NV |

TABLE 4 presents the comparative results. Compared with the engineering criterion, the SynCShapelet criterion of the STVS in this study significantly improved the accuracy of stability discrimination (approximately 20%). The notable improvement (approximately 2.5%) in the STVS discrimination accuracy stems from overcoming the interference of the commutation failure of the HVDC system. A comprehensive evaluation model combining the coupling of the MIHVDC and dynamic characteristics of the load was innovatively established. Feature decoupling of the dynamic evolution process of the power system was realized by constructing a nonlinear mapping relationship between the trajectory of the state quantity and distance space. Its discriminant effectiveness is reflected as follows: 1) the interactive influence of commutation failure and motor gridlock is considered; 2) the bifurcation characteristics of the critical subtrajectories in the STVS are captured; and 3) the contraction effect of the dynamic load recovery characteristics on the stability criterion is quantified.

| TABLE 4 ¦ Comparison with traditional engineering judgment. |  |  |  |
| --- | --- | --- | --- |
| Category | Engineering Judgment | Shapelet Feature Extraction Classification (Excluding DC Impact) | SynCShapelet Classification |
| Decision Rule | Binary Table: 0.8p.u., 10s | Decision Tree | Decision Tree |
| Monitoring Metric | Node Voltage Amplitude | Shapelet Candidate Distance | Shapelet Cluster Distance considering the transient interaction mechanism |
| Threshold Setting | Manually Set | Analysis Based on Operating Conditions and Bulk Response Data | Analysis Based on Operating Conditions and Bulk Response Data |
| Accuracy | 78% | 94.5% | 97% |

By integrating multi-dimensional shapelet-based time-series data mining, the proposed method provides a novel pathway for STVS assessment in complex MIHVDC systems, which can distinguish and resist commutation failure interference from HVDC systems. Additionally, elucidating their physical connection to the trajectory of traversing the critical slip is closely aligned with the STVS mechanism and effectively addresses the low credibility of machine learning techniques in STVS studies.

- | Conclusion

To address the intricate coupling challenges associated with high-dimensional, time-varying, and nonlinear factors in the evaluation of MIHVDC systems within STVS, this study devised a hybrid evaluation method that leverages interaction mechanisms across multiple timescales, along with data-driven feature extraction. This innovative approach effectively overcomes the limitations of traditional analytical methods, which struggle to quantify dynamic reactive power interaction processes. Moreover, it enhances the reliability of machine learning models in this context.

This study developed and validated an interaction mechanism across multiple timescales by categorizing the transient voltage instability process into three distinct time frames. The accumulation and transfer mechanisms of reactive power deficiencies were elucidated under various temporal conditions. Furthermore, a shapelet-based algorithm, SynCShapelet, was developed to capture the critical instability features associated with dynamic load–slip transitions by analyzing the transient response data of the system such as voltage and power. Our findings indicate a significant physical relationship between the segments identified by SynCShapelet and critical periods of instability. The STVS evaluation method presented in this study effectively classifies STVS and offers theoretical support for STVS assessment using a numerical example based on the power grid. The research findings indicate that SynCShapelet effectively enhances the distinctive features of the external system characteristics during transient interactions. This establishes a foundational mechanism for data-driven feature mining.

In future research, the segment identified by SynCShapelet will effectively distinguish the impact of the rapid dynamic processes in the DC system on the AC system and differentiate instability sequences across various voltage levels, thereby representing different types of instability. Future research should further broaden the scope of multi-objective optimization scenarios, such as incorporating dynamic interactions between new energy volatility and load uncertainty. Furthermore, it is essential to explore a real-time feature extraction framework to enhance both the real-time capabilities and robustness of large-scale power grid STVS assessments.

Acknowledge

This work was supported by National Natural Science Foundation of China-U22B6008.

References

[1] Reddy SA, Kumari MS. A review of switching overvoltage modeling in UHV AC transmission lines. Electric Power Systems Research. 2024;236:110902.http://doi.org/10.1016/j.epsr.2024.110902.

[2] Benato R, Sessa SD. The Ossanna’s Theorem for Educational Purposes: Impact of Distributed Parameter Transmission Lines on Power Systems. IEEE Access. 2021;9:10577-85.http://doi.org/10.1109/ACCESS.2021.3049395.

[3] Xu Z, Dong H, Huang H. Debates on ultra‐high‐voltage synchronous power grid: the future super grid in China? IET Generation, Transmission & Distribution. 2015;9:740-7.http://doi.org/10.1049/iet-gtd.2014.0281.

[4] Wang H, Zhang Y, Lin W, Wei W. Transregional electricity transmission and carbon emissions: evidence from ultra-high voltage transmission projects in China. Energy Economics. 2023;123:106751.http://doi.org/10.1016/j.eneco.2023.106751.

[5] Alamri B, Hossain MA, Asghar MJ. Electric power network interconnection: A review on current status, future prospects and research direction. Electronics. 2021;10:2179.http://doi.org/10.3390/electronics10172179.

[6] Garcia WRL, Tixador P, Raison B, Bertinato A, Luscan B, Creusot C. Technical and economic analysis of the R-type SFCL for HVDC grids protection. IEEE Transactions on Applied Superconductivity. 2017;27:1-9.http://doi.org/10.1109/TASC.2017.2739642.

[7] Renedo J, Rouco L, Garcia‐Cerrada A, Sigrist L. Transient stability versus damping of electromechanical oscillations in power systems with embedded multi‐terminal VSC‐HVDC systems. IET Generation, Transmission & Distribution. 2023;17:3477-87.http://doi.org/10.1049/gtd2.12874.

[8] Veerashekar K, Schuehlein P, Luther M. Quantitative transient stability assessment in microgrids combining both time-domain simulations and energy function analysis. International Journal of Electrical Power & Energy Systems. 2020;115:105506.http://doi.org/10.1016/j.ijepes.2019.105506.

[9] Odun-Ayo T, Crow ML. Structure-preserved power system transient stability using stochastic energy functions. IEEE Transactions on Power Systems. 2012;27:1450-8.http://doi.org/10.1109/TPWRS.2012.2183396.

[10] Muyeen S, Hasanien HM, Al-Durra A. Transient stability enhancement of wind farms connected to a multi-machine power system by using an adaptive ANN-controlled SMES. Energy Conversion and Management. 2014;78:412-20.http://doi.org/10.1016/j.enconman.2013.10.039.

[11] Poursaeed AH, Namdari F. Real-time voltage stability monitoring using weighted least square support vector machine considering overcurrent protection. International Journal of Electrical Power & Energy Systems. 2022;136:107690.http://doi.org/10.1016/j.ijepes.2021.107690.

[12] Singh P, Parida S, Chauhan B, Choudhary N. Online voltage stability assessment using artificial neural network considering voltage stability indices.  2020 21st National Power Systems Conference (NPSC): IEEE; 2020. p. 1-5.

[13] Vanfretti L, Arava VN. Decision tree-based classification of multiple operating conditions for power system voltage stability assessment. International Journal of Electrical Power & Energy Systems. 2020;123:106251.http://doi.org/10.1016/j.ijepes.2020.106251.

[14] Lashgari M, Shahrtash SM. Fast online decision tree-based scheme for predicting transient and short-term voltage stability status and determining driving force of instability. International Journal of Electrical Power & Energy Systems. 2022;137:107738.http://doi.org/10.1016/j.ijepes.2021.107738.

[15] Zhiyuan S, Mingpo L, Jie Z, Binjiang H, Guo Q, Yihua Z. Transient voltage stability assessment method based on gcForest.  Journal of Physics: Conference Series: IOP Publishing; 2021. p. 012025.

[16] Qu Y, Wang J, Cheng X, Hao J, Wang W, Niu Z, et al. Migratable Power System Transient Stability Assessment Method Based on Improved XGBoost. Energy Engineering. 2024;121.http://doi.org/10.32604/ee.2024.048300.

[17] Velayati MH, Amjady N, Khajevandi I. Prediction of dynamic voltage stability status based on Hopf and limit induced bifurcations using extreme learning machine. International Journal of Electrical Power & Energy Systems. 2015;69:150-9.http://doi.org/10.1016/j.ijepes.2015.01.005.

[18] Gök G, Salor Ö, Taplamacıoğlu MC. Transient event classification using pmu data with deep learning techniques and synthetically supported training-set. IET Generation, Transmission & Distribution. 2023;17:1287-97.http://doi.org/10.1049/gtd2.12734.

[19] Li Z, Yan J, Liu Y, Liu W, Li L, Qu H. Power system transient voltage vulnerability assessment based on knowledge visualization of CNN. International Journal of Electrical Power & Energy Systems. 2024;155:109576.http://doi.org/10.1016/j.ijepes.2023.109576.

[20] Rizvi SMH, Sadanandan SK, Srivastava AK. Data-driven short-term voltage stability assessment using convolutional neural networks considering data anomalies and localization. IEEE Access. 2021;9:128345-58.http://doi.org/10.1109/ACCESS.2021.3107248.

[21] Fu H, Wang Y, Liu Q, Zang B, Zhou S, Song W, et al. Lightning Stroke Transient Identification Method for HVDC Transmission Line based on DBN.  2022 IEEE/IAS Industrial and Commercial Power System Asia (I&CPS Asia): IEEE; 2022. p. 1944-9.

[22] Wang H, Chen Q, Zhang B. Transient stability assessment combined model framework based on cost‐sensitive method. IET Generation, Transmission & Distribution. 2020;14:2256-62.http://doi.org/10.1049/iet-gtd.2019.1562.

[23] Chen Y, Xie H. Transient voltage stability assessment based on an improved TCN-BiLSTM framework.  2022 IEEE 5th International Electrical and Energy Conference (CIEEC): IEEE; 2022. p. 4420-6.

[24] Yagami M, Ichinohe M, Tamura J. Enhancement of power system transient stability by active and reactive power control of variable speed wind generators. Applied Sciences. 2020;10:8874.http://doi.org/10.3390/app10248874

[25] Jiang H, Ma S, Zheng B, Ban L, Xiang Z. Application of SVG to mitigate voltage sag in energizing no-load transformer.  IET Conference Proceedings CP775: IET; 2020. p. 430-4.

[26] He Z, Zong W, Fan T. The effect of SVC on the transient stability simulation and analysis of Henan power grid. International Conference on Sustainable Power Generation and Supply (SUPERGEN 2012): IET; 2012. p. P03.

[27] Yang H, Zhu L, Cai Z, Chen Y, Li X. Influence of HVDC control on HVDC reactive power dynamic characteristic. Power System Technology. 2014;38:2631-7.http://doi.org/10.13335/j.1000-3673.pst.2014.10.003.

[28] Xiaohua L, Chao Y, Zexiang C. Influence of AC System Strength on Commutation in HVDC. Mechanical & Electrical Engineering Technology. 2016;45:67-74.http://doi.org/10.13335/j.1000-3673.pst.2014.10.003.