# Unified Mode Selection Framework for Real-Time VAr Optimization Tool in Unbalanced Distribution Systems

Hari Krishna Achuthan Parthasarathy, Student Member, IEEE, Zahra Soltani, Member, IEEE, and Mojdeh Khorsand, Member, IEEE

Abstract—High penetration of residential photovoltaic (PV) units has caused severe voltage issues in the distribution feeders. During seasons with low demand and high PV generation, distribution feeders face increasing power quality issues. Continuous operation in system conditions with these voltage issues reduces the lifetime of distribution equipment and can cause severe monetary loss. Legacy VAr support devices are too sparse and slow to mitigate these issues. With the introduction of the IEEE 1547-2018 standard, Distributed Energy Resources (DERs) are allowed to participate in providing VAr support to mitigate these issues. This paper proposes a novel Unified Mode Selection (UMS) framework within a real-time VAr optimization tool for distribution networks. This tool is developed based on an effective unbalanced distribution AC Optimal Power Flow (ACOPF) formulation. The proposed model has the ability to select between the Volt-VAr and Watt-VAr operational modes for each VAr enabled smart inverters, and to simultaneously optimize the controller set-points to optimally dispatch each inverter, minimizing operational costs and mitigating the voltage issues. The tool is tested on a snapshot of a distribution network in Arizona and compared against using only Volt-VAr or Watt-VAr operational mode with default settings. The results confirm the effectiveness of the model.

Index Terms—AC optimal power flow, Distributed Energy Resources (DERs), IEEE 1547-2018, Mode Selection, Setting Selection, Volt-VAr controller, Watt-VAr controller.

NOMENCLATURE

Sets and Indices

Kl	Set/Index of lines

Pi,j	Set/Index of nodes/buses

ϕφ,φ',φ''	Set/Index of phases

F1f	Set/Index of PV units with controllers

F2e	Set/Index of PV units without controllers

Parameters

Zlφ,φ'	Impedance (self: φ=φ', mutual: φ≠φ') of Line l between Phases φ and φ'

ylφ,φ'	Admittance (Self: φ=φ', Mutual: φ≠φ') of Line l between Phases φ and φ'

Lo,φT	No load loss of Transformer o at Phase φ

Di,φP	Active power demand at Bus i and Phase φ

Di,φQ	Reactive power demand at Bus i and Phase φ

M1	A large positive number

Ilmax,φ	Maximum line rating of Line l at Phase φ

Pf,φpvv,av	Available power generation of PV unit f∈F1 at Phase φ

Pf,φpvv,max	Active power rating of PV unit f∈F1 at Phase φ

Qf,φpvv,max	Reactive power rating of PV unit f∈F1 at Phase φ

Sf,φpvv,max	Apparent power rating of PV unit f∈F1 at Phase φ

Pe,φpv,av	Available power generation of PV unit e∈F2 at Phase φ

πs,φB	Wholesale electricity price at Substation s

πf,φpvvπe,φpv	Price of electricity produced by PV unit f∈F1/ e∈F2 at Phase φ

Variables

Ilr,φ	Real component of current in Line l at Phase φ

Ilim,φ	Imaginary component of current in Line l at Phase φ

Viφ	Voltage magnitude of Node i at Phase φ

Vir,φ	Real component of voltage of Node i at Phase φ

Viim,φ	Imaginary component of voltage of Node i at Phase φ

Iir,φ	Real component of net current injection in Node i at Phase φ

Iiim,φ	Imaginary component of net current injection in Node i at Phase φ

Pf,φpvv	Active power generation of PV unit f∈F1 at Phase φ

Qf,φpvv	Reactive power generation of PV unit f∈F1 at Phase φ

Ps,φB	Active power at Substation s at Phase φ

Qs,φB	Reactive power at Substation s at Phase φ

Qk,φC	Reactive power injected/absorbed by Capacitor Bank k at Phase φ

uf,φqv	Binary variable associated with zone selection for Volt-VAr mode of operation

uf,φpq	Binary variable associated with zone selection for Watt-VAr mode of operation

# I. INTRODUCTION

## A. Motivation and Background

Distributed Energy Resources (DERs) are playing an increasing role in many of power quality issues that affect the modern-day distribution systems. Residential Photovoltaic (PV) units are one such substantial factor, which are leading the wave in increasing DERs penetration levels in distribution systems. These units together tend to create fast voltage fluctuations, violation, and unbalance issues in the distribution feeders. Reactive power support is a popular solution to manage voltage violation issues. Legacy VAr support devices, e.g., On-Load Tap Changers (OLTCs), capacitor banks and voltage regulators, have several shortcomings related to fast voltage fluctuations [1]. Their speed and frequency of operation are in different time scales with respect to these fluctuations. These legacy VAr devices are not desired to be adjusted frequently [2], due to their maintenance cost. Coupled with the initial cost and sparsity of installation on the grid, these devices are not a viable solution.

With the advent of Smart Inverters (SIs) and the IEEE 1547-2018 standard [3], DERs currently have the ability to participate in mitigating voltage violations and unbalance issues by providing reactive power support. The standard introduces four different VAr control modes based on specified curve characteristics, which can be modified within an allowable range. Increased integration level of these DERs interfaced by SI provides the ability to control voltage at several different localized buses, which leads to a more economical and effective solution. This opportunity creates a need for a real-time operational scheduling framework, which can optimally identify the mode of operation, the settings, and the optimal amount of active and reactive power from each DER.

High R/X ratio of distribution systems makes them completely different from a transmission system, which implies that the same assumptions of DC Optimal Power Flow (DCOPF) cannot be applied. Moreover, the mutual coupling phenomenon cannot be ignored due to the untransposed nature and varying phasing of distribution systems, as well as the prevalence of single phase DERs. An operational scheduling framework for distribution systems is not complete without modeling these components but including them also adds to the distribution model complexity. There are many approaches which leverage linearization and assumptions to simplify the unbalanced distribution system model. LinDistFlow [4] is one such approach with strong assumptions such as ignoring line losses and nearly balanced bus voltages, which affects accuracy of the scheduling solution. Convex relaxation approaches such as Semi-Definite Programming (SDP) and Second Order Cone Programming (SOCP) are also used in the literature to convexify the non-linear and non-convex ACOPF. Reference [5] describes how convex relaxations cause expanded feasible regions, which may lead to infeasible solutions to the original model. The original non-linear non-convex ACOPF formulations are also affected by solution quality (due to local optima convergence) and scalability issues for Distribution Optimal Power Flow applications [6]. Therefore, there is a need for an operational scheduling framework, which is rapid for real-time operations, and accurately models the unbalanced distribution system and VAr capability of SIs. In addition, the tool should also optimally utilize the VAr capability to mitigate voltage issues.

## B. Literature Review

There are multiple reasons why legacy VAr control devices do not work against the issues raised by DERs. Reference [1] exhibits the limitations of conventional VAr devices such as OLTCs, switched capacitor banks and automatic voltage regulators. Although tap settings of OLTCs can be lowered in such a way to help deal with the voltage issues, the intermittent nature of PV units creates dynamic voltage fluctuations [1]. Reference [7] presents how voltage unbalance in a distribution feeder causes excessive thermal issues and reduction in lifetime for motor loads. Reference [8] introduces the effect of charging and discharging of Electric Vehicles (EVs) in causing voltage unbalance in low voltage distribution feeders. Interchanging connections between phases to equally redistribute loads [9], is a non-effective solution due to the fast nature of the voltage unbalance issues. Even with the advent of solid-state devices, the performance of legacy VAr devices with respect to fast voltage fluctuations, and their limited range of operation prevents them from being a viable solution. References [2] and [10] also mention the limitation in terms of the number of devices and the frequency of operations, which restrain them from regulating fast voltage fluctuations. Additionally considering the cost of installation and maintenance, legacy VAr devices are insufficient for effective voltage management in the modern grids.

The IEEE 1547-2018 standard [3] released by the IEEE Standards Coordinating Committee 21, allows DERs to participate in the VAr support through four different operational modes with clearly defined curves. Volt-VAr (Voltage-Reactive power) control, is one of the most utilized control modes among the four modes. Several previous studies investigate the efficacy of Volt-VAr control in different scenarios. Reference [11] utilizes the flexibility provided by solar PV units to minimize voltage unbalance in a distribution feeder. However, the reactive power dispatch from the PV units is constrained only by the capacity and does not follow the IEEE 1547 standard [3]. References [4], [12], and [13] utilize an unbalanced LinDist3Flow model for a distribution system with an assumption of ignoring line losses while modeling Volt-VAr curves. This assumption affects the accuracy of the dispatch solution. Furthermore, [4] and [13] model the Volt-Var curves which do not align with the IEEE 1547 standard requirements. References [14] and [15] present a VAr support strategy based on a SOCP-ACOPF formulation using the branch flow and DistFlow model, respectively, assuming a balanced distribution system. Reference [15] proposes a method  based on maximizing Conservation Voltage Reduction (CVR) savings with a Volt-VAr control curve which does not follow the IEEE 1547 standard [3]. Such dispatch set-points lead to real-time unavailability of the scheduled reactive power, as a SI would follow the curve as required by the IEEE 1547-2018 standard [16].

Reference [17] develops an unbalanced distribution OPF and models Volt-VAr curves in the first stage and the Volt-Watt curve in the second stage, where the voltage estimated by the first stage is applied as an input for the second stage. Volt-Watt is a control scheme, acting to curtail active power for voltages beyond 1.05 p.u., and does not align with the goals of a framework which attempts to actively manage voltage issues. Reference [12] optimizes the dispatch based on Volt-Watt and Volt-VAr operational modes, which do not follow IEEE 1547 allowable settings. Reference [18] compares eight different operational modes including the four listed in the IEEE 1547 standard which are modeled individually. The simulation in [18] is performed using a commercial power flow tool, on the model of a regional distribution system, with the voltage recorded over a 24-hour period. It should be noted that [12], [17]-[18] do not consider mode selection among the different operational modes of SIs.

A high R/X ratio corresponds to a strong coupling between voltage and active power. Active power injection curtailment of DERs is a viable strategy for limiting voltage issues in the distribution systems, but it imposes an increased operational cost due to the under-utilization of DERs. Watt-VAr (Active Power-Reactive Power) operational scheme provides a good balance when optimizing the dispatch of power considering voltage limits. Volt-VAr scheme, independent of active power injection, forces a certain amount of reactive power for a given voltage, which is not optimal for conditions where the apparent power injection is close to the inverter rating. References [19]-[21] present Watt-VAr operational schemes along with either an optimal power flow or a power flow scheme. References [19]-[20] compute the modified slope of the Watt-VAr curve with the help of voltage sensitivity metrices. Besides being computationally inefficient for real-time operation, using sensitivity metrices does not necessarily guarantee an optimal solution, but only yields a feasible solution. References [19]-[20] also present schemes which do not follow the set-points established by the IEEE 1547 standard [3]. Moreover, [19] presents an operational framework based on power flow, which implies that the active power dispatch is not controlled. Reference [21] presents an active and reactive power optimization strategy, based on a balanced pi-equivalent distribution system model. This model is further relaxed by using SDP. Moreover, [21] does not model any SI operational modes as specified by the IEEE 1547 standard [3].

To the best of the author’s knowledge, [22] is the only work which has attempted to create a mode selection formulation among four operational modes including Volt-Watt, Volt-VAr (P-priority), Volt-VAr (Q-priority) and constant power factor mode. A mixed integer nonlinear formulation is presented which is tested on an IEEE 123 bus system. According to the IEEE 1547 standard [3], Volt-Watt is an active power voltage operational mode, specified to be enabled along with one of the reactive power operational modes, i.e., it is not a mutually exclusive operational mode. Apart from scalability issues faced by nonlinear formulations [6], [22] also constrains rated reactive power to 48% of rated apparent power, which does not align with the 44% limit as prescribed by the IEEE 1547 standard [3]. With respect to the discussion above, the main contribution of this work is as follows.

- A set of piece-wise functions for Watt-VAr and Volt-VAr are modeled simultaneously within an ACOPF model, enabling optimal active and reactive power management in primary and secondary feeders.

- An additional set of constraints within the operational scheme are proposed to create the Unified Mode Selection (UMS) framework. The UMS framework optimally identifies and selects the required VAr control scheme for each bus equipped with an SI in the distribution feeder to manage voltage issues across the system.

- An approach is proposed to improve the performance of the UMS framework by concurrently performing optimal setting selection along with mode selection, establishing a co-optimized UMS framework.

- Two distinct formulations are proposed to mitigate unbalanced bus voltages in three-phase sections of the distribution feeders utilizing active and reactive power dispatch from PV units equipped with SIs.

The remaining sections of this work are organized as follows. Section II reviews the authors’ previously developed and published ACOPF model and formulation [16], [23]-[24], which is utilized for the proposed UMS framework of this paper. It is important to note that the proposed UMS framework could be applied to any other accurate unbalanced distribution ACOPF. Section III presents the formulation of the UMS and the co-optimized UMS. Section IV presents the results, and Section V concludes the work.

# II. Unbalanced Distribution OPF Model using the Current Voltage AC Optimal Power Flow (IVACOPF)

Representing the different elements of an unbalanced distribution system in an ACOPF formulation increases the model complexity. Using approximations to linearize this problem, such as the LinDistFlow [4] approach can simplify the model. Such approximations affect the model accuracy due to the assumptions such as nearly balanced bus voltages and ignoring line losses [24]. The Current Voltage AC Optimal Power Flow (IVACOPF) [16], [23]-[24] for distribution systems captures all distribution system complexities, including mutual impedance and admittance. The main objective of the VAr optimization tool with the UMS framework is to minimize costs related to purchasing substation power and maximize power from PV units, thus reducing operational cost as in (1).

minVir,φ, Viim,φ, Iir,φ,Iiim,φIlr,φ, Ilim,φ,Pf,φpvv,Qf,φpvv φ∈ϕ∀siπs,φBPs,φB+∀f∈F1iπf,φpvvPf,φpvv+∀e∈F2iπe,φpvPe,φpv 	(1)

Equation (2) depicts how the voltage differences across a line, at a phase, are affected by the currents and voltages in the other two phases. Voltage difference across Node i and Node j, connected by Phase φ of Line l is given by (2).

Viφ-Vjφ=φ'∈ϕZlφ,φ'Ilφ'-12φ'∈ϕZlφ,φ'φ''∈ϕylφ',φ''Viφ'',∀φ∈ϕ,l∈K	(2)

The real and imaginary parts of the net injection at Node i, at Phase φ, is given by (3) and (4).

Iir,φ=l∈hiIlr,φ,∀φ∈ϕ,i∈P	(3)

Iiim,φ=l∈hiIlim,φ,∀φ∈ϕ,i∈P	(4)

The active and reactive power balance constraints are represented by (5a), (5b), (6a) and (6b), where si, ki and di represent the set of substations, capacitor banks and demand buses respectively.

∀siPs,φB+∀f∈F1iPf,φpvv+∀e∈F2iPe,φpv-∀d∈diDi,φP-∀o∈oiLo,φT=Pi,φ,∀φ∈ϕ,i∈P	(5a)

Pi,φ=Vir,φIir,φ+Viim,φIiim,φ,∀φ∈ϕ,i∈P	(5b)

∀siQs,φB+∀f∈F1iQf,φpvv-∀d∈diDi,φQ-∀k∈kiQk,φC=Qi,φ ,∀φ∈ϕ,i∈P	(6a)

Qi,φ=Viim,φIir,φ+Vir,φIiim,φ,∀φ∈ϕ,i∈P	(6b)

Equations (5b) and (6b) are both non-convex and non-linear. Therefore, they are reformulated with linearized versions and solved iteratively, by using Taylor's Series First Approximation (TSFA) as shown in (7) and (8), where the superscript (t) implies that the term is a Taylor series parameter.

Pi,φ=Vir,φtIir,φ+Viim,φtIiim,φ+Vir,φIir,φt+Viim,φIiim,φt -Vir,φtIir,φt-Viim,φtIiim,φt,∀φ∈ϕ,i∈P	(7)

Qi,φ=Viim,φtIir,φ-Vir,φtIiim,φ+Viim,φIir,φt- Vir,φIiim,φt-Viim,φtIir,φt+Vir,φtIiim,φt,∀φ∈ϕ,i∈P	(8)

Voltage magnitude for each Node i, at Phase φ, is shown in (9). Equation (9) is also non-linear, as the voltage and current formulation is based on rectangular coordinates and is therefore reformulated as a linear constraint using TSFA as in (10).

Viφ=2Vir,φ2+Viim,φ2,∀φ∈ϕ,i∈P	(9)

Viφ=Vir,φtVir,φ2Vir,φ2t+Viim,φ2t+ Viim,φtViim,φ2Vir,φ2t+Viim,φ2t	(10)

The voltage limits at each Node i, and Phase φ, is given by (11). The thermal line rating for each Line l, at Phase φ, is given by (12). Reactive power limits for capacitor banks are given by (13).

0.95≤Viφ≤1.05, ∀φ∈ϕ,i∈P	(11)

Iir,φ2+Iiim,φ2≤Ilmax,φ2,∀φ∈ϕ,l∈K 	(12)

Qk,φC≤Qk,φC,max,∀φ∈ϕ,k∈ki	(13)

The PV units without controllers are unable to curtail active power. Active power from such PV units is given by (14).

Pe,φpv=Pe,φpv,av,∀φ∈ϕ,e∈F2 	(14)

The PV units equipped with PV controllers, i.e., VAr enabled SIs, are constrained by inverter apparent power limits, active power curtailment, and reactive power limits, represented by (15), (16) and (17).

Pf,φpvv2+Qf,φpvv2≤Sf,φpvv,max2,∀φ∈ϕ,f∈F1	(15)

Pf,φpvv≤Pf,φpvv,av,∀φ∈ϕ,f∈F1	(16)

-Qf,φpvv,max≤Qf,φpvv≤Qf,φpvv,max,∀φ∈ϕ,f∈F1	(17)

Apart from mitigating voltage violations, i.e., (11), two approaches are proposed to reduce voltage unbalance within the three phases of the distribution feeder as follows.

## A. Voltage Balancing Using Constraints

In this subsection, the mitigation of voltage unbalance is accomplished through formulating constraints which restrict Phase Voltage Unbalance Factor (PVUF; equation(18)) to two percent as prescribed by the IEEE Std 141-1993 [25]. Equations (19)-(21) constrain the voltage unbalance between phases of a three-phase bus to be within two percent as shown below.

PVUFi=Vi∆maxViavg,∀i∈PThree Phase	(18)

Viavg=∀φ∈ϕViφ3,∀i∈PThree Phase	(19)

Viavg-Viφ≤Vi∆max,∀φ∈ϕ,∀i∈PThree Phase	(20)

Vi∆max≤0.02×Viavg,∀i∈PThree Phase	(21)

Equation (20) contains an absolute difference which is reformulated linearly as shown in (22) and (23).

Viavg-Viφ≤Vi∆max,∀φ∈ϕ,∀i∈PThree Phase	(22)

Viφ-Viavg ≤Vi∆max,∀φ∈ϕ,∀i∈PThree Phase	(23)

## B. Voltage Balancing Using a Term in the Objective Function

In this subsection, the mitigation of voltage unbalance is achieved through modifying the objective function to minimize cost savings and system wide voltage unbalance. Balancing voltages strictly with constraints sets a hard bound. However, in extreme cases, where it is impossible to limit the unbalance system-wide to two percent, an objective function-based unbalance minimization can be utilized as shown in (24).

minVir,φ, Viim,φ, Iir,φ,Iiim,φIlr,φ, Ilim,φ,Pf,φpvv,Qf,φpvv φ∈ϕ∀siπs,φBPs,φB+∀f∈F1iπf,φpvvPf,φpvv+∀e∈F2iπe,φpvPe,φpv+wunbalance×∀i∈PThree PhaseVi∆,φ 	(24)

The wunbalance corresponds to the weight assigned to balancing voltages with respect to cost savings. The two components of the objective function are opposing in nature, considering the action taken to balance the system, involves active power curtailment and reactive power dispatch, which affects the operation cost. The absolute voltage deviation per phase Vi∆,φ in (24) is obtained as described in (25)-(27).

Viavg=∀φ∈ϕViφ3,∀i∈PThree Phase	(25)

Viavg-Viφ≤Vi∆,φ,∀φ∈ϕ,∀i∈PThree Phase	(26)

Viφ-Viavg ≤Vi∆,φ,∀φ∈ϕ,∀i∈PThree Phase	(27)

# III. unified Mode Selection (UMS) Scheme

With the introduction of the IEEE 1547-2018 standard, DERs are allowed to provide VAr support to mitigate voltage issues in the distribution feeder. This ability solves the issue of sparsity and operational performance compared to legacy VAr devices. However, DERs participation in VAr support and distribution feeder voltage management can be enhanced by an operational framework, capable of optimally selecting the mode and zone of operation for the SIs. The UMS scheme provide this versatility by combining the benefits of Watt-VAr and Volt-VAr operational modes, without adding significant computational complexity.

## A. Mode Selection with Default Settings of IEEE 1547

Volt-VAr and Watt-VAr operational modes, given fixed set-points, i.e., curve parameter settings, have different characteristics. The flexibility to choose between these two modes for each SI in the distribution feeder aids in mitigating voltage-issues without increased active power curtailment. The default set-points for Volt-VAr curve in IEEE 1547 [3], i.e., V1,φpvv,V2,φpvv,V3,φpvv,V4,φpvv in Fig. 1, are set to be 0.94 p.u., 0.98 p.u, 1.02 p.u, 1.06 p.u., respectively. The set-points for Watt-Var curve in IEEE 1547 [3], i.e., P3,φ'pvv,P2,φ'pvv,P1,φ'pvv,P1,φpvv,P2,φpvv,P3,φpvv in Fig. 2, are set to be 100% of Pf,φ'max,pvv, 40% of Pf,φ'max,pvv, 20% of Pf,φ'max,pvv, 20% of Pf,φmax,pvv, 40% of Pf,φmax,pvv, 100% of Pf,φmax,pvv, respectively.

Fig.  1 Volt-VAr characteristic curve according to the IEEE 1547 [3].

Fig.  2 Watt-VAr characteristic curve according to the IEEE 1547 [3].

Equation (28) is a piece-wise formulation of the Volt-VAr curve which is compliant with the IEEE 1547 standard [3].

Qf,φpvv=Qf,φpvv,max                ,Vf,φmin≤Viφ<V1,φpvvQf,φpvv,maxV2,φpvv-ViφV2,φpvv-V1,φpvv,V1,φpvv≤Viφ<V2,φpvv0                              ,V2,φpvv≤Viφ<V3,φpvvQf,φpvv,maxV3,φpvv-ViφV4,φpvv-V3,φpvv,V3,φpvv≤Viφ<V4,φpvv-Qf,φpvv,max             ,V4,φpvv≤Viφ<Vf,φmax	(28)

As shown in Fig. 1, the Volt-VAr curve has five different operating zones. The piece-wise function is formulated as a Mixed Integer Linear Programming (MILP) model using the Big-M method. The binary variable associated with zone selection in Volt-Var curve is represented in (29)-(38). Zone 1 is modeled as (29) and (30), wherein the SI injects maximum reactive power. Equations (31) and (32) represent Zone 2, where the SI injects reactive power according to a slope. The dead zone, i.e., Zone 3, as in Fig. 1, is given by (33) and (34). Equations (35) and (36) represent Zone 4, where the SI absorbs reactive power according to a slope. Zone 5 is modeled as (37) and (38), wherein the SI absorbs maximum reactive power.

Viφ≤M1u1,f,φqv+V1,φpvv	(29)

-M1u1,f,φqv≤Qf,φpvv-Qf,φpvv,max≤M1u1,f,φqv	(30)

-M1u2,f,φqv+V1,φpvv≤Viφ≤M1u2,f,φqv+V2,φpvv	(31)

-M1u2,f,φqv≤Qf,φpvv-Qf,φpvv,maxV2,φpvv-ViφV2,φpvv-V1,φpvv≤M1u2,f,φqv	(32)

-M1u3,f,φqv+V2,φpvv≤Viφ≤M1u3,f,φqv+V3,φpvv	(33)

-M1u3,f,φqv≤Qf,φpvv≤M1u3,f,φqv	(34)

-M1u4,f,φqv+V3,φpvv≤Viφ≤M1u4,f,φqv+V4,φpvv	(35)

-M1u4,f,φqv≤Qf,φpvv-Qf,φpvv,maxV3,φpvv-ViφV4,φpvv-V3,φpvv≤M1u4,f,φqv	(36)

-M1u5,f,φqv+V4,φpvv≤Viφ	(37)

-M1u5,f,φqv≤Qf,φpvv+Qf,φpvv,max≤M1u5,f,φqv	(38)

Figure 2 represents the Watt-VAr curve, with seven distinct zones of operation. The left half of the plane in the figure represents the zones of operation, applicable only when the DER can absorb active power, i.e., the DER includes a storage device such as Battery Energy Storage System (BESS). The curve compliant to the IEEE 1547 standard [3], is modeled as a piece-wise function as in (39).

Qf,φpvv=Qf,φpvv,max                         ,Pf,φpvv<P3,φ'pvvQ2,φ'pvv+P2,φ'pvv-Pf,φpvvQ3,φ'pvv-Q2,φ'pvvP2,φ'pvv-P3,φ'pvv,P3,φ'pvv≤Pf,φpvv<P2,φ'pvvQ1,φ'pvv+P1,φ'pvv-Pf,φpvvQ2,φ'pvv-Q1,φ'pvvP1,φ'pvv-P2,φ'pvv,P2,φ'pvv≤Pf,φpvv<P1,φ'pvvQ1,φpvv+P1,φpvv-Pf,φpvvQ1,φ'pvv-Q1,φpvvP1,φpvv-P1,φ'pvv,P1,φ'pvv≤Pf,φpvv<P1,φpvvQ2,φpvv+P2,φpvv-Pf,φpvvQ1,φpvv-Q2,φpvvP2,φpvv-P1,φpvv,P1,φpvv≤Pf,φpvv<P2,φpvvQ3,φpvv+P3,φpvv-Pf,φpvvQ2,φpvv-Q3,φpvvP3,φpvv-P2,φpvv,P2,φpvv≤Pf,φpvv<P3,φpvv-Qf,φpvv,max                  ,P3,φpvv≤Pf,φpvv	(39)

The Watt-VAr curve is modeled as a mixed integer formulation, using Big-M method as represented in (40)-(53). Zone 1, where the PV unit injects maximum reactive power, is represented by (40) and (41). Equations (42) and (43) represent Zone 2, wherein the PV injects reactive power in a linear fashion. Equations (44) and (45) represent Zone 3, wherein the PV injects reactive power according to a slope. Zone 4 is modeled by (46) and (47), in which if Q1,φpvvand Q1,φ'pvvare set to zero. Zone 5 is formulated by (48) and (49), in which the PV absorbs reactive power linearly. Zone 6 is formulated by (50) and (51), in which the PV absorbs reactive power according to a slope. Equation (52) and (53) represent Zone 7, in which the PV absorbs rated reactive power.

Pf,φpvv≤M1u1,f,φpq+P3,φ'pvv	(40)

-M1u1,f,φpq≤Qf,φpvv-Qf,φpvv,max≤M1u1,f,φpq	(41)

-M1u2,f,φpq+P3,φ'pvv≤Pf,φpvv≤M1u2,f,φpq+P2,φ'pvv	(42)

-M1u2,f,φpq≤Qf,φpvv-Q2,φ'pvv+P2,φ'pvv-Pf,φpvvQ3,φ'pvv-Q2,φ'pvvP2,φ'pvv-P3,φ'pvv≤M1u2,f,φpq	(43)

-M1u3,f,φpq+P2,φ'pvv≤Pf,φpvv≤M1u3,f,φpq+P1,φ'pvv	(44)

-M1u3,f,φpq≤Qf,φpvv-Q1,φ'pvv-P1,φ'pvv-Pf,φpvvQ2,φ'pvv-Q1,φ'pvvP1,φ'pvv-P2,φ'pvv≤M1u3,f,φpq	(45)

-M1u4,f,φpq+P1,φ'pvv≤Pf,φpvv≤M1u4,f,φpq+P1,φpvv	(46)

-M1u4,f,φpq≤Qf,φpvv-Q1,φpvv-P1,φpvv-Pf,φpvvQ1,φ'pvv-Q1,φpvvP1,φpvv-P1,φ'pvv≤M1u4,f,φpq	(47)

-M1u5,f,φpq+P1,φpvv≤Pf,φpvv≤M1u5,f,φpq+P2,φpvv	(48)

-M1u5,f,φpq≤Qf,φpvv-Q2,φpvv-P2,φpvv-Pf,φpvvQ1,φpvv-Q2,φpvvP2,φpvv-P1,φpvv≤M1u5,f,φpq	(49)

-M1u6,f,φpq+P2,φpvv≤Pf,φpvv≤M1u6,f,φpq+P3,φpvv	(50)

-M1u6,f,φpq≤Qf,φpvv-Q3,φpvv-P3,φpvv-Pf,φpvvQ2,φpvv-Q3,φpvvP3,φpvv-P2,φpvv≤M1u6,f,φpq	(51)

-M1u7,f,φpq+P3,φpvv≤Pf,φpvv	(52)

-M1u7,f,φpq≤Qf,φpvv+Qf,φpvv,max≤M1u7,f,φpq	(53)

Equation (54) represents the mutual exclusivity constraint, restricting the selection of multiple zones of operation at the same time. The mode of operation arises intrinsically from the above approach and does not require explicitly modeling mode selection as a decision process with binary variables. Therefore, the proposed approach reduces the number of binary variables required for the model, reducing computational complexity.

u1,f,φqv+u2,f,φqv+u3,f,φqv+u4,f,φqv+u5,f,φqv+u1,f,φpq+u2,f,φpq+u3,f,φpq+u4,f,φpq+u5,f,φpq+u6,f,φpq+u7,f,φpq≤11,∀f∈F1	(54)

## B. Mode Selection with Co-optimized Settings

According to the IEEE 1547 standard [3], the set-points for the Volt-VAr and Watt-VAr modes of operation can be modified within an allowable range. Consequently, the UMS scheme can be modified to optimally choose set-points of each control curve as shown in Fig. 3.

Fig.  3 Operational mode and set-point Co-optimization of a SI.

Equations (55)-(58) constrain the set-points of Volt-VAr mode of operation, V1,φpvv,V2,φpvv,V3,φpvv, and, V4,φpvv, which are optimally selected, compliant to the IEEE 1547 standard:

0.82≤V1,φpvv≤V2,φpvv-0.02 	(55)

0.97≤V2,φpvv≤1.00	(56)

1.00≤V3,φpvv≤1.03	(57)

V3,φpvv+0.02≤V4,φpvv≤1.18 	(58)

Equations (59)-(64) constrain the set-points of Watt-VAr mode of operation, P3,φ'pvv,P2,φ'pvv,P1,φ'pvv,P1,φpvv,P2,φpvv and, P3,φpvv, which are optimally selected, compliant to the IEEE 1547 standard:

Pf,φ'pvv,max≤P3,φ'pvv≤P2,φ'pvv+0.1×Pf,φ'pvv,max	(59)

0.8×Pf,φ'pvv,max≤P2,φ'pvv≤0.4×Pf,φ'pvv,max	(60)

P2,φ'pvv-0.1×Pf,φ'pvv,max≤P1,φ'pvv<0	(61)

0<P1,φpvv≤P2,φpvv-0.1×Pf,φpvv,max	(62)

0.4×Pf,φpvv,max≤P2,φpvv≤0.8×Pf,φpvv,max	(63)

P2,φpvv+0.1×Pf,φpvv,max≤P3,φpvv≤Pf,φpvv,max	(64)

Modifying set-points within the framework makes constraints (32), (36), (43), (45), (47), (49) and (51) non-convex and nonlinear. The above-mentioned constraints are reformulated as MILP constraints using TSFA, where superscript (t) implies that the term is the corresponding Taylor series parameter. Equation (32) can be reformulated as,

-M1u2,f,φqv≤Qf,φpvv-V2,φpvvt-ViφtQf,φpvv,maxV2,φpvvt-V1,φpvvt+Qf,φpvv,maxtViφV2,φpvvt-V1,φpvvt-Qf,φpvv,maxtV2,φpvvt-ViφtV1,φpvvV2,φpvvt-V1,φpvvt2+Qf,φpvv,maxtV1,φpvvt-ViφtV2,φpvvV2,φpvvt-V1,φpvvt2≤M1u2,f,φqv	(65)

Similarly, (36) can also be reformulated as a MILP constraint using TSFA. Equation (66) gives a bound on the maximum reactive power set-point for each iteration for Volt-VAr scheme and Watt-VAr scheme of operation.

-Qf,φpvv,maxt≤Qf,φpvv,max≤Qf,φpvv,maxt	(66)

where Qf,φpvv,maxt for the first iteration is initialized with the maximum reactive power capability of the SIs as prescribed by the IEEE 1547 standard. Equation (43) can be reformulated as a MILP constraint using the same technique, as shown in (67).

-M1u2,f,φpq≤Qf,φpvv-Q2,φ'pvvt-Q3,φ'pvvt-Q2,φ'pvvt P2,φ'pvvt-Pf,φpvvt P2,φ'pvvt-P3,φ'pvvt- Pf,φpvvt-P3,φ'pvvtQ2,φ'pvv-Q2,φ'pvvt P2,φ'pvvt-P3,φ'pvvt- P2,φ'pvvt-Pf,φpvvtQ3,φ'pvv-Q3,φ'pvvt P2,φ'pvvt-P3,φ'pvvt-Q3,φ'pvvt-Q2,φ'pvvt Pf,φpvvt-P3,φ'pvvtP2,φ'pvv-P2,φ'pvvt P2,φ'pvvt-P3,φ'pvvt2-Q3,φ'pvvt-Q2,φ'pvvt P2,φ'pvvt-Pf,φpvvtP3,φ'pvv-P3,φ'pvvt P2,φ'pvvt-P3,φ'pvvt2+ Q3,φ'pvvt-Q2,φ'pvvtPf,φpvv-Pf,φpvvt P2,φ'pvvt-P3,φ'pvvt≤M1u2,f,φpq	(67)

Similarly, (45), (47), (49) and (51), can also be reformulated as MILP constraints using TSFA. Equations (68)-(73) bound each reactive power set-point to the respective ranges for Watt-VAr scheme, according to the IEEE-1547-2018 standard.

-Qf,φpvv,max≤Q3,φ'pvv≤Qf,φpvv,max	(68)

-Qf,φpvv,max≤Q2,φ'pvv≤Qf,φpvv,max	(69)

-Qf,φpvv,max≤Q1,φ'pvv≤Qf,φpvv,max	(70)

-Qf,φpvv,max≤Q1,φpvv≤Qf,φpvv,max	(71)

-Qf,φpvv,max≤Q2,φpvv≤Qf,φpvv,max	(72)

-Qf,φpvv,max≤Q3,φpvv≤Qf,φpvv,max	(73)

During the co-optimization process, to facilitate improved convergence, step-size factors ε1and ε2 are introduced to bound the set-points of the Volt-VAr and Watt-VAr operational modes after the first iteration, as shown by the examples in (74) and (75).

V1,φpvvt-ε1≤V1,φpvv≤V1,φpvvt+ε1	(74)

P1,φpvvt-ε2≤P1,φpvv≤P1,φpvvt+ε2	(75)

# IV. Simulation Studies and Validation

The proposed framework is tested using data of an actual distribution system in Arizona. This distribution  system is a 12.5 kV, 9 km long distribution feeder, which includes both primary (12.5 kV) and secondary (120-240V load level) sections . The extensive model includes 8095 buses, 7943 lines and 742 PV units. More information about this test system is presented in [26]. This distribution feeder has an installed residential rooftop PV capacity of 3.8 MW, which is one of the highest PV penetration levels among the distribution feeders of this utility. The snapshot is from a case of over-voltage on March 15, 2019, at 2 PM during spring, which typically has high active power output of PVs and reduced demand due to mild weather in March. Due to SI VAr capability being inactive, the units injected maximum active power available at unity power factor, which caused over-voltage conditions, as shown in Fig. 4.

Fig.  4 Voltage profile of primary feeder prior to VAr optimization

At the time of the snapshot, the PV inverters injected 3.625 MW of active power, compared to 1.563 MW of active power demand which roughly translates to a 232% instantaneous PV penetration without a voltage management strategy. The convex model of the VAr optimization tool, is formulated as a Mixed Integer Quadratic Programming (MIQP) problem and is implemented through Python using Pyomo. The proposed formulation is solved using Gurobi, which is a commercial MILP solver. The optimization is performed on a laptop with an Intel i9-12900H CPU, 32GB DDR4 and 1TB PCIe SSD. The prices for the PV generation and the wholesale price are obtained from Pacific Gas & Electric (PG&E) surplus compensation [27] and the locational marginal price map from California Independent System Operator (CAISO) [28] for the area respectively. Two cases are presented to analyze the performance of each VAr scheme as proposed in the above sections. The first case focuses on the performance of SIs with respect to over-voltage issues caused due to increased penetration of PVs. For Case I, the locations of VAr capability enabled SIs are obtained from a previous work [29], which involves the optimal placement of PV controllers. The second case aimed at the performance of SIs with respect to voltage-unbalance issues within the feeder, for which a modified testing system with increased penetration is presented.

TABLE I

Feeder-Wide PV Generation and Curtailment over Different VAr-Operational modes

| No. Of SIs (¦F1¦) | Volt-VAr (kW) |  | Watt-VAr (kW) |  | UMS-D (kW) |  | UMS-C (kW) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PGenPV | PCurPV | PGenPV | PCurPV | PGenPV | PCurPV | PGenPV | PCurPV |
| 110 | 707 | 0 | 707 | 0 | 707 | 0 | 707 | 0 |
| 85 | 481 | 107 | 521 | 67 | 533 | 55 | 538 | 50 |
| 75 | 272 | 261 | 324 | 209 | 384 | 161 | 386 | 159 |
| 70 | 223 | 283 | 266 | 239 | 324 | 181 | 327 | 179 |

## A. Case I: Over-Voltage Mitigation

As shown in Fig. 4, prior to VAr optimization, the feeder experienced severe over-voltage issues. The system wide performance of the specific VAr operational modes is analyzed for four modes, i.e., Volt-VAr with default settings, Watt-VAr with default settings, UMS scheme with default settings, and UMS scheme with co-optimized settings, over different sets of VAr enabled SIs: 110, 85, 75, and 70 out of the total 742 PV inverters. Table I presents the results obtained over different sets of PV units, across different VAr control modes. As the number of VAr enabled SIs reduce, the ability to inject or absorb reactive power decreases. Therefore, more active power is curtailed to mitigate voltage issues. PV active power curtailment possibly increases due to two reasons: 1) strong active power-voltage coupling in distribution systems which imply a sharp reduction in voltage with curtailment. 2) Curtailment due to an inability to absorb reactive power, as apparent power ratings of the SIs are reached. Across different VAr operational modes, greater flexibility implies better gains. Mode Selection Default (UMS-D) offers greater flexibility and thus performs significantly better than Volt-VAr alone and Watt-Var alone control modes. Simultaneously optimizing the curve settings offers minimal gains between Mode Selection Default and Mode Selection Co-optimized (UMS-C) VAr control modes for the existing scenario. Figure 5 exhibits active power dispatch of each VAr operational mode for the case of seventy VAr enabled SIs. Volt-VAr control mode performs the worst on average across all buses due to an inability to absorb an adequate amount of reactive power, causing increased curtailment. Comparatively, Watt-VAr performs better, as the reactive power absorption mitigates any potential over-voltage issues. However, due to the fixed nature of the curve, regardless of bus voltage, Watt-VAr tends to over-absorb reactive power. This over-absorption infringes on the ability to inject active power, as the SI reaches the apparent power limit. Figure 5 depicts the Watt-VAr dispatch points where over-absorption leads to reduction in active power dispatch.

Fig.  5 Active Power Profile of SIs with 70 VAr enabled SIs

TABLE II

Maximum TSFA Error and Computation Times for the IVACOPF

| No. Of SIs (¦F1¦) | TSFA Error and Computation Time |  |  |
| --- | --- | --- | --- |
|  | Active Power (kW) | Reactive Power (kVAr) | Computation Time (min) |
| 110 | 2.0e-03 | 2.0e-03 | 3.1 |
| 85 | 1.6e-03 | 1.6e-03 | 3.0 |
| 75 | 1.3e-04 | 1.3e-04 | 3.0 |
| 70 | 6.1e-02 | 6.1e-02 | 3.1 |

Figure 6 represents how over-absorption of reactive power may lead to lower voltages at buses locally but causes higher voltages at other adjacent buses, due to higher reactive power injection from primary sections of the feeder to compensate for over-absorption of reactive power in this scheme. For example, while comparing voltage profiles in cases of Watt-VAr and Volt-VAr inverter operation modes, Bus 2587 experiences a 0.0028 p.u. increase in voltage in Watt-Var operation mode. This voltage increase is a result of higher reactive power injection from the primary sections of the feeder to this bus, which is caused by a higher reactive power absorption in the neighboring bus, Bus 8401, which absorbs 1.435 kVAr more reactive power for Watt-VAr compared to Volt-VAr.

UMS-D has the flexibility to select the right VAr control model based on reactive power needs to prevent this issue as shown in Fig.7. UMS-C expands this flexibility by finding the margin of need by optimally choosing set-points for the selected mode of operation. In Fig. 7, the Watt-VAr control mode absorbs more reactive power than Volt-VAr control mode as represented by the two distinct regions. UMS-D and UMS-C optimally choose the modes at each bus. There are several instances where reactive power absorption drops to zero or close to zero in only the UMS-C results. On these buses, the other three modes are over-absorbing reactive power which reflects on the curtailment metrics. The optimization is performed over the different sets of VAr enabled SIs and VAr operational modes while updating Taylor series parameters in three iterations. Over the three iterations, the approximation converges well within the nominal values as shown in Table II. The computation times of all VAr operational modes are the total run times corresponding to three iterations. The TSFA error on average, for active power and reactive power are insignificant by the third iteration. As discussed in [24], the substantial accuracy improvement of the IVACOPF over the widely used LinDistFlow model, is pertinent in modeling prevalent single phase DERs with SIs and their characteristics.

Fig.  6 Feeder wide relative voltage difference with respect to UMS-D

Fig.  7 Reactive power profile of SIs with VAr enabled SIs

## B. Case II: Voltage Unbalance Mitigation

To test the efficacy of the framework to handle issues such as voltage unbalance, the test system is modified. Voltage unbalance occurs due to reasons such as unevenly distributed loads and generation amongst the three phases in a feeder. The modification is performed by increasing the penetration of PV in a single phase. Excessive amounts of active power generation in a single phase creates excessive amounts of unbalance with the other two phases. The UMS scheme is utilized to balance these voltages by scheduling the SIs to mitigate the issue without curtailing PV generation. 230 additional PV units are added in the secondary sections of the original feeder, in phase two alone. This increased penetration caused significant voltage violations and unbalance issues across the primary and secondary sections of the feeder.

Fig.  8 Voltage profile of primary sections of the feeder prior to VAr optimization

The net injection from the 972 PV units was 5.221 MW compared to 1.563 MW of active power demand, which roughly translates to a 334% instantaneous PV penetration. As shown in Fig. 8, severe voltage issues are observed, with maximum bus voltage at 1.082 p.u. and PVUFs exceeding two percent at three-phase sections. Two approaches to alleviate the abovementioned voltage issues are validated below.

- Voltage Balancing Using Constraints

The proposed model of Section II. A is tested on different cases with varying numbers of VAr enabled SIs to analyze the efficacy of the method for various level of sparsity of VAr enabled SIs along the feeder. The voltage profile of the primary sections of the feeder, post-optimization, are shown in Fig. 9, for a case of 340 VAr enabled SIs. Table III presents the net unbalance of the system and the curtailment metrics of PV generation. In general, UMS-C performs better over the different sets of VAr enabled SIs. In cases with less number of VAr enabled SIs, the ability to inject or absorb reactive power reduces. In such cases, curtailment of active power aids in voltage reduction and voltage balancing. Therefore, as the number of VAr enabled SIs decrease, the active power curtailment increases.

Fig.  9 Voltage profile of primary sections of the feeder after VAr optimization

TABLE III

PV curtailment and Maximum Voltage Unbalance Metrics for Different Sets of VAr enabled SIs

| No. Of SIs (¦F1¦) | UMS-D |  | UMS-C |  |
| --- | --- | --- | --- | --- |
|  | PCurPV (kW) | PVUF (%) | PCurPV (kW) | PVUF (%) |
| 340 | 957.7 | 0.6032 | 916.85 | 0.5657 |
| 330 | 1032.4 | 0.5515 | 972.9 | 0.5521 |
| 320 | 1042.9 | 0.5445 | 994.3 | 0.5343 |
| 310 | 1185.6 | 0.4434 | 1156.7 | 0.4345 |
| 300 | 1333.3 | 0.3803 | 1308.1 | 0.3445 |

Fig.  10 PVUF profile of the three phase sections of the feeder, prior to and after VAr optimization.

The maximum PVUFs across the feeder are also presented in Table III. Prior to VAr optimization, PVUFs across the feeder exceeded two percent. After optimization, maximum PVUF is reduced to 0.6 percent. As shown in Fig. 10, the overall PVUF profile across the three-phase sections of the feeder exhibits drastic improvement. UMS-C, in every instance, performs on par or better than UMS-D due to the added flexibility from optimally choosing set-points. This flexibility enables the scheme to inject more active power while maintaining PVUF at a nominal value.

- Voltage Balancing Using Objective Functions

To compare the performance of UMS-D and UMS-C, different weights, i.e., wunbalance in the objective function of (24), are considered. Table IV presents the curtailment of PV units with each weight considering both the modes.

TABLE IV

Net PV curtailment for Different Weights of the Balancing Objective

| Weight wunbalance | UMS-D Curtailment (kW) | UMS-C Curtailment (kW) |
| --- | --- | --- |
| 0 | 955.90 | 914.35 |
| 1 | 959.71 | 917.40 |
| 10 | 1009.68 | 939.34 |
| 20 | 1060.71 | 995.38 |
| 25 | 1215.93 | 1102.68 |
| 30 | 1308.51 | 1213.46 |
| 40 | 1369.56 | 1329.81 |
| 50 | 1489.45 | 1485.63 |
| 70 | 1538.33 | 1645.90 |
| 90 | 1574.50 | 1670.60 |
| 100 | 1588.96 | 1714.55 |

As the weight to balance voltage in the system, wunbalance, increases, the active power curtailment increases to mitigate voltage unbalance. As mentioned previously, PV active power curtailment possibly increases due to two reasons: 1) strong active power-voltage coupling implying a sharp reduction in voltage with curtailment. 2) Curtailment due to an inability to absorb reactive power, i.e., close to SI apparent power rating. Considering (24), as the weight increases, UMS-D seemingly performs better than UMS-C with respect to curtailment. Figure 11 presents the comparison of system wide voltage unbalance ∀φ∈ϕ∀i∈PThree PhaseVi∆,φ with respect to the PV active power curtailment. Each point on the plot represents a specific weight, i.e., wunbalance, applied to the objective, for the specific UMS scheme chosen. The weights are plotted in ascending order. As the weight of the balancing component increases, unbalance decreases and consequently, curtailment increases. The curve representing UMS-C entirely lies underneath the curve  corresponding to UMS-D. Therefore, at every instance, UMS-C yields a better curtailment metric for a specified amount of system unbalance, compared to UMS-D. The pareto optimal solution can be obtained, such that the PVUF is balanced with the objective of cost savings and curtailment, at the operator’s discretion.

Fig.  11 System wide net voltage deviation with respect to curtailment.

V. Conclusions

In this paper, a real-time VAr optimization tool is proposed using the UMS framework for an unbalanced distribution system with the main objective of minimizing operational costs. The UMS framework is formulated with default settings for both Watt-VAr and Volt-VAr operational curves based on the IEEE 1547-2018 standard [3]. An extension on the formulation is presented, to concurrently optimize the set-points of the VAr curves. The performance of these operational schemes are compared against using only Volt-VAr or Watt-VAr operational modes to mitigate over-voltage issue. Two distinct approaches are also presented to effectively manage the voltage unbalance in the feeder caused by increased PV penetration. The results exhibit the flexibility offered by the two UMS schemes in mitigating system voltage issues in a computationally effective manner. Comparison of pareto front solutions show that UMS-C offers substantial improvements to UMS-D while considering both active power curtailment and voltage unbalance metrics. The results also illustrate how sparsity of VAr enabled SIs in the system and various system conditions affect VAr enabled SIs performance. Therefore, there is a need for effective and economical voltage management strategies in distribution systems with high DER penetration. The authors also acknowledge the need to coordinate legacy VAr devices with VAr support from SIs to maximize effectiveness, which is left for the future work.

# References

[1]	N. Mahmud and A. Zahedi, “Review of control strategies for voltage regulation of the smart distribution network with high penetration of renewable distributed generation” in Ren. and Sust. Ene. Rev., vol.64, pp 582-595, 2016.

[2]	X. Sun, J. Qiu, and J. Zhao, “Optimal Local Volt/Var Control for Photovoltaic Inverters in Active Distribution Networks” in IEEE Tran. on Pow. Sys., vol. 36, pp. 5756-5766, 2021.

[3]	IEEE Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces, IEEE Std 1547™-2018, 2018.

[4]	D. B. Arnold, et al, “Optimal dispatch of reactive power for voltage regulation and balancing in unbalanced distribution systems” in 2016 IEEE PESGM, Boston, MA, USA, 2016, pp. 1-5.

[5]	Y. Liu, J. Li, and L. Wu, “ACOPF for three-phase four-conductor distribution systems: semidefinite programming-based relaxation with variable reduction and feasible solution recovery” in IET Gen. Tran. Dist., vol. 13, pp. 266-276, 2019.

[6]	R. R. Jha et al., “Distribution Grid Optimal Power Flow (D-OPF): Modeling, Analysis, and Benchmarking” in IEEE Tran. on Pow. Sys., vol. 38, pp. 3654-3668, 2023.

[7]	M. Karimi, et al., “Photovoltaic penetration issues and impacts in distribution network – A review” in Ren. and Sust. Ene. Rev., vol 53, pp 594-605, 2016.

[8]	F. Shahnia, et al. “Predicting Voltage Unbalance Impacts of Plug-in Electric Vehicles Penetration in Residential Low-Voltage Distribution Networks.” in Elec. Pow. Comp. and Sys., vol. 41, pp. 1594–616, 2013.

[9]	T. A. Short, “Electric Power Distribution Handbook”. Boca Raton, FL, USA: CRC, 2004.

[10]	M. M. Rezvani, et al., “Interaction of Transmission-Distribution System in the Presence of DER Units–Co-simulation Approach” in IEEE Open Jou. of Ind. App., vol. 1, pp. 23-32, 2020.

[11]	K. Girigoudar and L. A. Roald, “On the impact of different voltage unbalance metrics in distribution system optimization” in Elec. Pow. Sys. Res., vol. 189,  no.106656, 2020.

[12]	A. Inaolaji, A. Savasci and S. Paudyal, “Distribution Grid Optimal Power Flow in Unbalanced Multiphase Networks with Volt-VAr and Volt-Watt Droop Settings of Smart Inverters” in IEEE Tran. on Ind. App., vol. 58, pp. 5832-5843, 2022.

[13]	A. Savasci, et al, “Two-Stage Volt-VAr Optimization of Distribution Grids with Smart Inverters and Legacy Devices” in IEEE Tran. on Ind. App., vol. 58, pp. 5711-5723, 2022.

[14]	M. Farivar, et al, “Optimal inverter VAR control in distribution systems with high PV penetration” in 2012 IEEE PESGM, San Diego, CA, USA, pp. 1-7, 2012.

[15]	A. Savasci, et al, “Distribution Grid Optimal Power Flow Integrating Volt-Var Drop of Smart Inverters” in 2021 IEEE GreenTech, Denver, CO, USA, pp. 54-61, 2021.

[16]	Z. Soltani, et al., “Volt-VAr Optimization of PV Smart Inverters in Unbalanced Distribution Systems,” in 2023 IEEE PESGE, San Diego, CA, USA, pp. 1-6, 2023.

[17]	R. Wagle, et al, “Optimal power flow based coordinated reactive and active power control to mitigate voltage violations in smart inverter enriched distribution network”, Int. Jou. of Green Ene., vol. 21:2, pp 359-375, 2023.

[18]	M. N. Acosta, et al., “Optimal Reactive Power Control of Smart Inverters: Vestfold and Telemark Regional Network” in 2021 IEEE PowerTech, Madrid, Spain, pp. 1-6, 2021.

[19]	A. Samadi, et al., “Coordinated Active Power-Dependent Voltage Regulation in Distribution Grids with PV Systems” in IEEE Tran. on Pow. Del., vol. 29, pp. 1454-1464, 2014.

[20]	A. Safayet, et al., “Reactive Power Management for Overvoltage Prevention at High PV Penetration in a Low-Voltage Distribution System” in IEEE Tran. on Ind. App., vol. 53, pp. 5786-5794, 2017.

[21]	E. Dall’Anese, et al., “Optimal Dispatch of Photovoltaic Inverters in Residential Distribution Systems” in IEEE Tran. on Sust. Ene., vol. 5, pp. 487-497, 2014.

[22]	T. O. Olowu, et al., “Optimal Mode and Droop Setting of Smart Inverters” in 2023 IEEE PESGM, Orlando, FL, USA, pp. 1-5, 2023.

[23]	Z. Soltani, et al., “Simultaneous Robust State Estimation, Topology Error Processing, and Outage Detection for Unbalanced Distribution Systems” in IEEE Tran. on Power Sys., vol. 38, pp. 2018-2034, 2023.

[24]	Z. Soltani, M. Khorsand and S. Ma, “Current–Voltage Unbalanced Distribution AC Optimal Power Flow for Advanced Distribution Management System Applications” in IEEE Open Jou. of Ind. App., vol. 5, pp. 155-167, 2024.

[25]	IEEE Recommended Practice for Electric Power Distribution for Industrial Plants, IEEE Std 141-1993, 1994.

[26]	K. Montano-Martinez et al., “Detailed Primary and Secondary Distribution System Model Enhancement Using AMI Data” in IEEE Open Acc. Jou. of Pow. and Ene., vol. 9, pp. 2-15, 2022.

[27]	Pacific Gas and Electric (PG&E), CA, USA, “Net Surplus Compensation Rates for Energy.” [Online]. Available: https://www.pge.com/pge\_global/common/pdfs/solar-and-vehicles/green-energy-incentives/AB920\_RateTable.pdf.

[28]	California ISO (CAISO), CA, USA, “Market Price Map.” [Online]. Available: http://www.caiso.com/PriceMap/Pages/default.aspx.

[29]	M. Chen, et al., “Optimal Placement of PV Smart Inverters with Volt-VAr Control in Electric Distribution Systems” in IEEE Sys. Jou., vol. 17, pp. 3436-3446, 2023.

The authors are with the School of Electrical, Computer, and Energy Engineering, Arizona State University, Tempe, AZ 85281 USA (e-mail: hpartha1@asu.edu; zsoltani@asu.edu; mabdikho@asu.edu). This work was supported by the DOE ARPA-E OPEN 2018 Program (DE-AR0001001) and Power System Engineering Research Center (M-44).