Broadband Harmonic Oscillation Suppression Strategy for Distribution Networks with High Penetration of Distributed Generation Using Direct-Mounted Damping Devices

Chengjia Bao 1, 2, 3, Tong Zhang 1, Yonggang Li 1, Tianyi Zhang 3 Jianwen Li 1, Rong Li 1,

1 State Key Laboratory of Alternate Electrical Power System with Renewable Energy Sources, North China Electric Power University, Yonghua North Street No. 619, Baoding, China.

2 State Grid Gansu Electric Power Company, Lanzhou, China.

3 Lanzhou Power Supply Subsidiary Company of State Grid Gansu Electric Power Co., Ltd.  Lanzhou, China.

Correspondence: Yonggang Li, School of Electrical and Electronic Engineering, North China Electric Power University, Yonghua North Street No. 619, Baoding, People's Republic of China

Email:51350586@ncepu.edu.cn

Funding:

National Fundamental Research Funds for the Central Universities, China (2024MS111).

Conflict of interest:

None

Permission statement to reproduce the materials from the other sources.

None

Data Availability Statement:

The data that support the findings of this study are available from the corresponding author upon reasonable request.

Abstract: In power systems with high penetration of distributed generations (DGs), multi-modal broadband harmonic oscillations pose a serious threat to secure and stable operation. Existing active and passive damping methods are limited in their capability to effectively suppress resonance peaks. Considering background harmonics and system impedance characteristics, this paper proposes a novel direct-mounted damping device to suppress broadband harmonic oscillations in the distribution network. In accordance with IEC specified electromagnetic compatibility standards for low-voltage grids, a unified quantitative indicator for broadband oscillation analysis is established. Additionally, a general procedure for damping device parameter design is developed based on modal analysis and the particle swarm optimization (PSO) algorithm. Simulation results show that the proposed topology achieves superior broadband oscillation suppression. Experiments on a multi-inverter grid-connected system further demonstrate the generality and effectiveness of the proposed method in suppressing multi-modal broadband harmonic oscillations within high-DG-penetration distribution networks.

Keywords: Harmonic Oscillations; Resonance Peaks; Passive Damping; Impedance Characteristics; Distribution Network; Low-Voltage Grids

Introduction

With the increasing penetration of distributed generations (DGs) and the widespread integration of power electronic devices into distribution networks, power systems exhibit low inertia, weak damping, and insufficient voltage support[1, 2]. Broadband background harmonics, high density inverter connections (both grid-connected and islanded), diverse inverter operating modes, and significant transmission power fluctuations increase the likelihood of harmonic oscillations across multiple frequency bands following system disturbances, leading to severe distortion of grid-connected waveforms[3, 4]. When these oscillations propagate to the load side, they can impair electrical equipment and further impact the main grid, potentially leading to large-scale power outages and compromising the safety and stability of the entire system[5, 6].

The impedance-based modeling approach enables effective stability analysis of distribution networks with high DG penetration. By representing DG as a single-port impedance, the resonance characteristics of a network composed of multiple port impedances can be analyzed[7]. The magnitude–frequency response of the equivalent impedance indicates the extent of harmonic amplification[8], while its phase–frequency response characterizes system stability[9]. Broadband oscillations can be mitigated by regulating both the magnitude and phase characteristics. Depending on the approach, suppression strategies are classified into inverter-level active damping methods and station-level passive damping methods[10-25]. The active damping method introduces proportional and differential links into the inverter control loop to suppress resonance peaks [10–12], or employs a virtual impedance in parallel at the point of common coupling (PCC), combined with frequency-domain passivity theory[13], to enhance the stability margin of grid-connected inverters (GCIs)[14, 15]. In multi-inverter grid-connected systems, the presence of numerous nonlinear control links makes it difficult to effectively suppress multiple resonance peaks simultaneously through parameter optimization or additional control methods, as current research still focuses on parameter design for specific control structures[16,17], and the methods lack general applicability.

The passive damping method reshapes the system impedance by connecting passive devices in parallel at the aggregation point of DGs. Commonly used devices include passive filters[18–22], static var generators (SVGs), and transformer windings[23–25]. Passive filters are further classified by order into second-order[18, 19], third-order[20, 21], and fourth-order types[22]. However, most existing passive damping methods focus on constraining the system impedance phase to ensure that phase jumps at resonance peaks do not exceed 180°. Although this prevents oscillatory divergence under harmonic disturbances, the waveform remains severely distorted because the system damping is nearly zero[22, 23]. The inductor filtering method proposed in [25] effectively shifts the system resonance point and enhances system damping to suppress oscillations, but it requires redesigning the transformer winding topology, making the method difficult to implement in practice. The multimodal resonance peaks observed in systems with high DG penetration result from the coupling of multiple LC passive networks. Damping serves as an effective indicator of resonance peak magnitude. Lower damping corresponds to higher resonance peak magnitudes and reduced system stability. By focusing on the magnitude frequency characteristics of system port impedance and aiming to improve system damping, reshaping the system impedance through parallel passive devices at the station level can effectively mitigate broadband harmonic oscillations caused by interactions between background harmonics and impedance networks.

The primary objective of parallel passive devices is to suppress multimodal resonance peaks and enhance the system’s operational stability margin, while minimizing associated fundamental-frequency losses. In high DG penetration distribution networks, the coupled impedance network often exhibits multiple series–parallel resonance modes. Selecting appropriate nodes to simultaneously mitigate multiple resonance modes has therefore become a pressing challenge. Moreover, conventional passive devices are limited by their inherent topological structures, making it difficult to achieve effective broadband resonance suppression. Developing novel passive devices with broadband tunability to suppress harmonic oscillations under complex operating conditions has become an important research focus. It is well established that parallel passive devices inevitably interact with the original system impedance network. Traditional parameter design methods that rely solely on background harmonic currents fail to meet the requirements of high DG penetration distribution networks. Avoiding the introduction of new resonance points during parameter design, while effectively enhancing system damping to suppress resonance peaks and quantitatively evaluate damping effects, remains a key technical challenge to be addressed.

Building upon the above background, this paper first employs modal analysis to investigate the oscillation characteristics of a system comprising two GCIs, thereby identifying key nodes for mitigating multiple oscillation modes. Based on a comparative study of three common passive filter types, a novel direct-mounted damping device is proposed. The port characteristics and oscillation suppression mechanism of the proposed device are systematically analyzed. A parameter design methodology is developed to minimize fundamental frequency losses and suppress the system’s multimodal resonance peaks. Considering the IEC-specified electromagnetic compatibility (EMC) levels for low-voltage distribution networks, a unified quantitative indicators for broadband oscillation analysis is established. The device parameters are subsequently optimized using a particle swarm optimization (PSO) algorithm. Simulation results demonstrate that the proposed damping device achieves high effectiveness in broadband oscillation suppression. Experimental validation on a multi-inverter grid-connected system further confirms the generality and effectiveness of the proposed method in suppressing multimodal broadband harmonic oscillations within high DG penetration distribution networks.

Gray box impedance modeling and oscillation mode analysis of GCI system

- 2.1  Grey-Box Impedance Modeling

Topology of the typical LCL grid-connected inverter (GCI) is shown in Fig. 1.

Fig. 1 Topology of LCL GCI system

Here, L1 is the inverter-side inductance, C is the filter capacitor, L2 is the grid-side inductance, and Lg is the equivalent grid inductance. Vdc denotes the inverter DC-side voltage, uinv, uC, uPCC and ug denote the inverter AC-side output voltage, the filter-capacitor voltage, the PCC voltage, and the grid voltage, respectively. iL1 is the inverter-side inductor current, iC is the filter capacitor current, and iL2 is the grid-connected current.

Based on the impedance analysis method[7], the inverter can be modeled as a one-port network characterized by an equivalent output impedance. Fig. 2 depicts the equivalent circuit of two GCIs system.

Fig. 2 Equivalent circuit of two GCIs system

For the two inverters (i = 1, 2), the equivalent current sources are denoted isi, and the grid-connected currents are denoted . Their equivalent impedances are denoted Zouti and , respectively. The two inverters are connected in parallel at Node 3. The total grid current is denoted ig, and the grid’s equivalent impedance is Zg.

Under practical operating conditions, the inverter’s terminal and internal parameters are often unknown (e.g., due to manufacturer confidentiality). Therefore, a disturbance-injection approach is adopted: broadband harmonic perturbations are injected at PCC to measure the frequency response of the terminal (port) impedance. Subsequently, a rational transfer-function model of the terminal impedance is identified using the vector-fitting (VF) algorithm. The resulting form is given in Eq. (1).

(1)

Table 1 lists the numerator and denominator coefficients of the Zouti in Eq. (1), as well as the inductance values.

Table 1 Parameters of the two GCIs system

| Parameters | Values | Parameters | Values |
| --- | --- | --- | --- |
| a0 | 2.075·1025 | c0 | 0.00018 |
| a1 | 3.0·1026 | c1 | 6.009·1025 |
| a2 | 1.8·1029 | c2 | 3.0·1025 |
| b0 | 9.24·1020 | c3 | 1.8·1028 |
| b1 | 1.68·1022 | d0 | 4.2·1018 |
| b2 | 1.008·1025 | d1 | 1.855·1020 |
| L21 | 0.425mH | d2 | 9.975·1026 |
| L22 | 0.36mH | Lg | 1mH |

By substituting the parameters from Table 1 into Eq. (1), Fig. 3 presents a comparison of the frequency response curves obtained from the fitted and measured impedance data.

Fig. 3 Comparison of frequency response curves obtained from impedance measurement and vector fitting

As shown in Fig. 3, within the frequency range of 10² – 10⁴ Hz, the fitted impedance agrees well with the measured data, confirming the accuracy of the impedance model derived using the VF algorithm.

From the magnitude–frequency characteristics in Fig. 3, the GCI system exhibits two pole – zero pairs, labeled p1, z1, p2, and z2, in ascending frequency. These features arise from parallel and series resonance interactions introduced by the two GCIs. The resonance magnitudes are substantially higher than those at neighboring frequencies. Consequently, if background grid harmonics coincide with these resonant frequencies, the impedance network can be excited into broadband harmonic oscillations.

From the phase–frequency characteristics in Fig. 3, the GCI terminal impedance exhibits predominantly inductive behavior across a broad frequency range. Phase transitions occur only in the neighborhoods of adjacent resonant peaks, at which the terminal impedance becomes capacitive. Therefore, to attenuate these resonances using an external shunt device, the device should present capacitive impedance over a wide frequency band. When connected in parallel (e.g., at PCC), the shunt branch offsets the system’s broadband inductive behavior and thereby suppresses multiple resonant peaks.

- 2.2 Identification of Key Nodes for Oscillation Suppression

Modal analysis method is employed to identify the system’s oscillation modes[26, 27]. The excitability, observability, and participation factors of each node with respect to these modes are calculated. The results are presented in Table 2.

Table 2 Resonant modal analysis results of the GCIs system

|  |  | 1 | 2 | 3 |
| --- | --- | --- | --- | --- |
| 1 (712Hz) | Excitability | 0.839∠0° | 0.297∠-0.25° | 0.457∠-0.05° |
|  | Observability | 0.839∠0.07° | 0.297∠-0.19° | 0.457∠0.13° |
|  | P.F. | 0.703 | 0.088 | 0.208 |
| 2 (2752Hz) | Excitability | 0.05∠0° | 0.917∠0° | 0.396∠0.03° |
|  | Observability | 0.05∠0° | 0.917∠0° | 0.396∠0.01° |
|  | P.F. | 0.003 | 0.841 | 0.157 |

Table 2 indicates that the system depicted in Fig. 2 exhibits two resonance modes: Mode 1 at 780 Hz and Mode 2 at 3425 Hz. Mode 1 has the highest participation factor at Node 1, indicating that Node 1 is the most excitable and observable location for this mode. Mode 2 exhibits the highest participation factor at Node 2, implying that Node 2 is the most excitable and observable for this mode. Node 3 exhibits significant excitability and observability in both modes. Therefore, connecting a shunt device at Node 3 to reshape the system impedance can effectively suppress oscillations in both modes.

Design Criteria for Direct-Mounted Damping Device

The primary purpose of parallel passive device is to attenuate multimodal resonance peaks in high DG penetration distribution network and enhance system damping. Additionally, the fundamental-frequency loss introduced by parallel connection must be taken into account. The parameter design should ensure that the loss remains below the specified threshold while effectively mitigating broadband harmonic oscillations in the system. The following sections provide a detailed discussion of these aspects.

- 3.1 Selection of Passive Devices

To mitigate harmonic oscillations in the system, various passive filters have been employed in engineering practice, including the RLC-based second-order filter [19], the Siemens-proposed third-order filter [28], and the Class C filter commonly used in HVDC transmission systems [20,21]. The topology and frequency response of these filters are illustrated in Fig. 4. and the parameters are shown in Table 3.

Fig. 4 Typical passive filter topologies and frequency response curves for broadband oscillation suppression Table 3 Parameters of the passive filter

| Parameters | C1f | C2f | L1f | Rf |
| --- | --- | --- | --- | --- |
| Values | 15μF | 8μF | 10mH | 500Ω |

The magnitude–frequency curves in Fig. 4 show that Fig. 4a) and 4c) each exhibit one resonance peak, caused by the series resonance of the inductor and capacitor branches in their respective topologies. In Fig. 4b), two resonance peaks appear, corresponding to the series resonance of L1fC1f and the parallel resonance of L1f(C1f∥C2f).

The phase–frequency curves in Fig. 4 show that all three configurations are capacitive at low frequencies. At high frequencies, Fig. 4a) and 4c) exhibit resistive behavior, while Fig. 4b) remains capacitive. The capacitive branches tend to amplify high-frequency harmonic currents. Since the inverter itself acts as a harmonic source and produces numerous high-frequency components, the passive device should exhibit resistive characteristics at high frequencies. Furthermore, when multiple inverters are coupled to the grid, multiple series and parallel resonances appear in the system. Therefore, the parallel passive device must include both series and parallel resonant branches to suppress these resonant peaks simultaneously. Based on this analysis, a new passive filter—termed the direct-mounted damping device—is proposed. Its topology and the port admittance’s frequency response are illustrated in Fig. 5.

Fig. 5 Topology and frequency response curves of the direct-mounted damping device

Fig. 5 illustrates that the direct-mounted damping device comprises two inductors (L1d and L2d), two capacitors (C1d and C2d), and a resistor (R1d). L1d and C1d form a series-resonant branch, while L2d and C2d constitute a parallel-resonant branch. The resistor R1d provides damping for the resonant branches. The frequency response curve displays two resonant peaks: the device behaves capacitively at low frequencies and inductively near both resonance points. At higher frequencies, its impedance gradually transitions from capacitive to resistive. The port characteristics of this device are complementary to that of the GCI system shown in Fig. 3. By properly designing the inductance and capacitance parameters and connecting the damping device in parallel, the broadband inductive characteristics of the system’s port impedance can be effectively reduced, thereby suppressing resonant peaks. This topology integrates the advantages of the passive filters shown in Fig. 4b) and 4c). The following section presents the parameter design procedure based on the device structure.

- 3.2 Upper Limits of Parameters for Direct-Mounted Damping Device

The expression for the port impedance of the direct-mounted damping device is derived from Fig. 5a) :

(2)

The primary function of capacitor C1d is to isolate the fundamental-frequency current component of the system. At the fundamental frequency, its impedance can be approximated as Zd ≈ 1 / sC1d.

Let the equivalent impedance of the grid be Zg = sLg; then, the energy-loss percentage loss ηloss after applying the direct-mounted damping device can be expressed as:

(3)

If the loss ratio is specified to be below 1%, the upper limit of the damping-device capacitance C1d can be determined as follows:

(4)

As shown in Fig. 5a), L1d and C1d together form the series-resonant branch of the direct-mounted damping device, which provides a path for harmonic currents. If the value of L1d is excessively large, the fundamental frequency loss of the device will increase significantly. The resonant frequency of the L1d and C1d branch should be greater than or equal to the third-harmonic frequency. Accordingly, the upper limit of L1d can be determined as follows:

(5)

Once the upper limit of C1d is established, the corresponding upper limit of L1d can be determined. C2d and L2d together form the parallel-resonant branch of the direct-mounted damping device. Their values determine the port-impedance characteristics of the device in the mid and high frequency ranges. The values of C2d and L2d should not exceed those of C1d and L1d, in order to avoid degrading the low-frequency impedance characteristics. The resistor R1d provides damping within the parallel-resonant branch, facilitating the rapid dissipation of harmonic currents. Therefore, R1d should be determined in conjunction with the upper and lower limits of L1d, L2d, C1d and C2d, as well as the system’s damping settings, to ensure that the damping device effectively suppresses resonant peaks in the mid and high frequency ranges.

- 3.2 Quantitative Indicators of Harmonics in high DG Penetration Distribution Networks

The damping coefficient ξ, a key parameter determining the system’s resonant-peak magnitude, effectively quantifies the degree of resonance suppression. However, ξ is limited by the system configuration, electrical parameter distribution, and energy dissipation mechanisms; thus, a universal value cannot be prescribed. Instead, ξ should be determined according to prevailing grid operating conditions. Consequently, a unified quantitative indicator suitable for broadband oscillation analysis must first be established. Drawing on the electromagnetic-compatibility levels of practical low-voltage distribution networks, a feasible reference value for ξ can be proposed to guide the design of damping device parameters.

IEC 61000-2-2 and IEC 61000-3-15 respectively define the harmonic-voltage limits for low-voltage distribution networks and the harmonic-current limits for grid-connected DG systems[29,30]. The corresponding limit values are listed in Table 4.

It is known that the response expression of the inverter under harmonic disturbance is given by Φ1 [8], and its general form can be expressed as follows:

(6)

In eq. (6),  ωs, ωn, ξ denote the angular frequency of harmonic excitation, the natural resonant frequency associated with the system’s characteristic root, and the corresponding equivalent damping coefficient, respectively.

When ωs equals ωn, the following relationship holds:

(7)

The grid harmonic voltage is considered as the excitation, while the grid-connected current of the DG serves as the response. The ratio of these two quantities represents the amplification factor (Φ1) of the response under the corresponding harmonic excitation. Subsequently, the critical damping coefficient (ξ) satisfying the harmonic limit requirements of the DG’s grid-connected current can be determined. The corresponding results are presented in Table 4.

Table 4 Critical damping coefficient for compliance with DG current harmonic limits (IEC 61000-3-15)

| Harmonic Order | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Low voltage grid harmonic limits | 2 | 5 | 1 | 6 | 0.5 | 5 | 0.5 | 1.5 | 0.5 | 3.5 | 0.458 | 3 | 0.429 |
| DG harmonic limits | 2 | 30 | 2 | 10 | 2 | 7 | 2 | 5 | 2 | 3 | 2 | 3 | 2 |
| Harmonic amplification factor Φ1 | 1 | 6 | 2 | 1.7 | 4 | 1.4 | 4 | 3.3 | 4 | 0.9 | 4.4 | 1 | 4.7 |
| critical value of ξ | 0.5 | 0.08 | 0.25 | 0.3 | 0.125 | 0.357 | 0.125 | 0.15 | 0.125 | 0.58 | 0.115 | 0.5 | 0.107 |
| Harmonic Order | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 |
| Low voltage grid harmonic limits | 0.4 | 0.406 | 2 | 0.389 | 1.761 | 0.375 | 0.3 | 0.364 | 0.1408 | 0.354 | 1.274 | 0.346 | 0.2 |
| DG harmonic limits | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 3 |
| Harmonic amplification factor Φ1 | 7.5 | 4.9 | 1.5 | 5.1 | 1.7 | 5.3 | 10 | 5.5 | 2.1 | 5.6 | 2.4 | 5.8 | 15.0 |
| critical value of ξ | 0.067 | 0.102 | 0.333 | 0.097 | 0.294 | 0.094 | 0.05 | 0.091 | 0.235 | 0.089 | 0.212 | 0.087 | 0.033 |
| Harmonic Order | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 |
| Low voltage grid harmonic limits | 0.339 | 1.061 | 0.333 | 0.975 | 0.328 | 0.2 | 0.324 | 0.833 | 0.319 | 0.773 | 0.316 | 0.2 | 0.313 |
| DG harmonic limits | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 | 3 | 2 |
| Harmonic amplification factor Φ1 | 5.9 | 2.8 | 6.0 | 3.1 | 6.1 | 15.0 | 6.2 | 3.6 | 6.3 | 3.9 | 6.3 | 15 | 6.4 |
| critical value of ξ | 0.085 | 0.177 | 0.083 | 0.163 | 0.082 | 0.033 | 0.081 | 0.139 | 0.08 | 0.129 | 0.079 | 0.033 | 0.078 |

Table 4 indicates that the harmonic voltage distribution in the low-voltage network follows a consistent pattern. Specifically, the harmonic magnitude decreases with increasing order. Adjacent odd-order harmonics are generally larger than the corresponding even-order ones, except for the 3rd order and its integer multiples, which are comparatively lower. The damping ratio (ξ) required to meet the harmonic limits of DG grid-connected currents is higher for odd orders and lower for even orders. Therefore, the pole (resonant) frequency of the distribution network should be placed as close as possible to an even-order harmonic, and the corresponding pole eigenvalue should maintain a damping ratio of ξ ≥ 0.2 to satisfy the harmonic-limit requirements for DG grid connection.

- 3.3 General Procedure for Parameter Design of Direct-Mounted Damping Device

Based on the above analysis, the fundamental frequency loss caused by the direct-mounted damping device can be kept below a specified threshold by appropriately setting the upper limits of its parameters. Parameter design should take the system’s characteristic roots as the primary optimization objective. Specifically, the following conditions should be satisfied:

- 1) After connecting the parallel damping device, the system’s resonant frequency should be close to an even-order harmonic, where the imaginary part of the characteristic root equals an integer multiple of 2π·100;

2) The damping ratio corresponding to the characteristic root should satisfy ξ ≥ 0.2 to ensure system stability.

Particle Swarm Optimization (PSO) is an algorithm characterized by strong convergence and fast search performance. It has been widely applied to the parameter design of passive filter devices and is adopted here as the optimization algorithm for determining the damping device parameters[31]. The detailed parameter design procedure is illustrated in Fig. 6.

Fig. 6 Procedure for the parameter design of the direct-mounted damping device

Verification of the Direct-Mounted Damping Device’s Effectiveness in Multi-Modal Resonance Suppression

The equivalent grid inductance of the system shown in Fig. 2 is 1 mH. Based on this value, the upper limits of the parameters of the direct-mounted damping device are determined to ensure that the fundamental frequency loss remains below 1%. The calculated upper-limit parameter values are presented in Table 5.

Tab.5 Upper limit of the direct-mounted damping device

| Parameter | Values |
| --- | --- |
| C1d /μF | 102 |
| C2d / μF | 102 |
| L1d / mH | 11 |
| L2d / mH | 11 |
| R1d / Ω | 1000 |

As analyzed in Section 2.2, connecting the direct-mounted damping device in parallel at node 3 of the system shown in Fig. 2 enables the simultaneous suppression of two pairs of resonant modes. The system’s nodal admittance matrix Y is used as input to the PSO algorithm, and the admittance expression of the damping device (Yd) is substituted into node 3 of Y (see the Appendix for details of Yd). The number of particles is set to 70, and the maximum number of iterations is 100. The upper and lower bounds of the parameters C1d, C2d, L1d, L2d, and R1d are defined as [10-6, 1.02×10-4]F, [10-6, 1.02×10-4]F, [10-4, 0.011]H, [10-4, 0.011]H, and [10-1, 103]Ω, respectively. The objective function is defined as follows: for all conjugate complex characteristic roots of matrix Y, the equivalent damping coefficient ξ must satisfy ξ ≥ 0.2, and the remainder n obtained by dividing the imaginary part of the root by (2π·100) must be an integer. The optimization results obtained through iteration are presented in Table 6.

Tab.6 Iteration results of the damping device

| Parameter | Values |
| --- | --- |
| C1d /μF | 84 |
| C2d / μF | 82 |
| L1d / mH | 9.38 |
| L2d / mH | 2.29 |
| R1d / Ω | 30.54 |

The parameters given in Table 6 are substituted into the direct-mounted damping device to obtain the system’s frequency-response curves before and after its installation, as shown in Fig. 7.

Fig.7 System frequency response before and after applying the parallel direct-mounted damping device

As shown in Fig. 7, the parallel connection of the direct-mounted damper effectively modifies the system’s port impedance, shifts its resonant frequency, and suppresses the two resonant peaks. The system’s characteristic roots, resonant frequencies, and damping ratios (ξ) are calculated before and after the damper is connected in parallel, and the results are presented in Table 7.

Tab.7 Characteristic roots, resonant frequencies and damping coefficient ξ under 2 operating conditions

|  | Parallel resonance characteristic root | Resonant frequency (Hz) | ξ | Series resonance characteristic root | Resonant frequency (Hz) | ξ |
| --- | --- | --- | --- | --- | --- | --- |
| Original system | λ1,2 = -7.67 ± j95.62 | 15 | 0.08 | λ1,2 = -15.63 ± j136.04 | 22 | 0.11 |
|  | λ3,4 = -6.53 ± j4908.1 | 781 | 0.00133 | λ3,4 = -1.86 ± j7269.2 | 1157 | 0.00026 |
|  | λ5,6 = -9.76 ± j21525 | 3426 | 0.00045 | λ5,6 = -6.46 ± j25197 | 4010 | 0.00026 |
| After connecting Direct-mounted Damping Device in Parallel | λ1 = -1.00 | / | / | λ1 = -1.00 | / | / |
|  | λ2 = -482.12 | / | / | λ2 = -481 | / | / |
|  | λ3,4 = -7.65 ± j95.56 | 15 | 0.08 | λ3,4 = -15.63 ± j136.04 | 22 | 0.11 |
|  | λ5,6 = -753.84 ± j5020.6 | 799 | 0.15 | λ5,6 = -1345.4 ± j7514.6 | 1196 | 0.18 |
|  | λ7,8 = -1903.3 ± j21376 | 3402 | 0.09 | λ7,8 = -1784.2 ± j25134 | 4000 | 0.07 |
|  | λ9 = -190570 | / | / |  |  |  |

As shown in Table 7, the original system exhibits two pairs of series–parallel resonance points at 781Hz, 1157Hz, 3426Hz, and 4010Hz, where the corresponding damping ratios (ξ) are relatively low. After the damping device is connected in parallel, the system’s resonant frequencies shift to 799 Hz, 1196 Hz, 3402 Hz, and 4000 Hz, which are all even harmonics. The corresponding ξ values increase significantly compared with those of the original system, consistent with the results in Fig. 7 and confirming the effectiveness of the proposed method and algorithm.

Verification of Conclusions

  - Simulation Verification

- 5.1.1 Operating Characteristics of the Original System Under Harmonic Disturbances

The two GCIs system shown in Fig. 2 was modeled in MATLAB/Simulink, and the corresponding parameter settings are provided in Table 1. As indicated in Table 7, the original system exhibits two pairs of series–parallel resonance points: parallel resonances occur at 781 Hz and 3426 Hz, while series resonances appear at 1157 Hz and 4010 Hz. These findings are verified in the following section.

A parallel harmonic current source was applied at node 3 of the system in Fig. 2. The harmonic current amplitude was set to 2% of the rated grid current, with frequencies of 781 Hz and 3426 Hz, respectively. The simulation duration was 0.5 s. Fig. 8 presents the voltage waveforms and FFT spectra of uC1 at node 1, uC2 at node 2, and uPCC at node 3.

Fig. 8 Node voltage waveforms and FFT spectra under harmonic current disturbance

As illustrated in Fig. 8, when background harmonic currents are present in the grid and their frequencies coincide with the system’s parallel resonance points, the voltage waveforms at each node exhibit noticeable distortion. In particular, the 15th harmonic in the uC1 waveform and the 69th harmonic in the uC2 waveform are significantly amplified, while both harmonics are simultaneously amplified in uPCC. These results agree well with the modal analysis findings in Table 2, indicating that the oscillation modes are most easily excited and observed at nodes with the largest participation factors. Consequently, the voltage waveforms at each node experience severe distortion, exceeding the harmonic limits required for GCI systems.

A series harmonic voltage source was applied to the grid, with an amplitude equal to 2% of the rated grid voltage. The harmonic frequencies were set to 1157Hz and 4010Hz, respectively, and the simulation duration was 0.5 s. Fig. 9 presents the waveforms and FFT spectra of the grid currents ig1 of inverter 1, ig2 of inverter 2, and the total grid current ig.

Fig. 9 Branch current waveforms and FFT spectra under harmonic voltage disturbance

As shown in Fig. 9, when background harmonic voltages are present in the grid and their frequencies coincide with the system’s series resonance points, the current waveforms in each branch exhibit noticeable distortion. In particular, the 23rd harmonic in ig1 and the 80th harmonic in ig2 are significantly amplified, while both harmonics are also amplified in the total grid current ig. Consequently, the branch currents become severely distorted, exceeding the harmonic limits required for GCI systems.

The simulation results in Fig. 8 and 9 confirm that the distribution networks with insufficient damping are highly susceptible to severe broadband harmonic oscillations induced by small disturbances, resulting in low system stability.

- 5.1.2 Operating Characteristics of the System After Connecting the Direct-Mounted Damping Device in Parallel

A direct-mounted damping device was connected in parallel at node 3 of the system shown in Fig. 2. Topology of the device is presented in Fig. 5a), and its parameters are provided in Table 6. As indicated in Table 7, after the device is connected in parallel, the system’s parallel resonant frequencies shift to 799 Hz and 3402 Hz, while the series resonant frequencies shift to 1196 Hz and 4000 Hz. These results are verified in the following section.

A harmonic current source was injected at node 3 of the system in Fig. 2. The current amplitude was set to 2% of the rated grid current, with harmonic frequencies of 799 Hz and 3402 Hz. The simulation duration was 0.5 s. Fig. 10 presents the waveforms and FFT spectra of uPCC, ig, and the branch current id of the damping device.

Fig. 10 Waveforms and FFT spectra with parallel damping device under harmonic current disturbance

As illustrated in Fig. 10, after the damping device is connected in parallel, when background harmonic currents are present in the grid and their frequencies coincide with the system’s parallel resonance points, neither uPCC nor ig exhibits harmonic oscillations, and waveform distortion remains minimal. The FFT spectra show that the total harmonic distortion (THD) of uPCC is 1.10%, and that of ig is 1.69%, both satisfying the harmonic limits for GCI system. In contrast, the id waveform contains abundant harmonics and exhibits significant distortion. Its FFT results indicate a fundamental current amplitude of 6.10 A and a THD of 15.91%, demonstrating that most harmonic currents in the grid are absorbed by the damper branch. Moreover, the small capacitance of C1d isolates the majority of the fundamental-frequency current, thereby minimizing the fundamental-frequency losses introduced by the parallel damping device.

A series harmonic voltage source was applied to the grid, with an amplitude equal to 2% of the rated grid voltage. The harmonic frequencies were 1196 Hz and 4000 Hz, and the simulation duration was 0.5 s. Fig. 11 presents the waveforms and FFT spectra of uPCC, ig, and id under harmonic voltage disturbance.

Fig.11 Waveforms and FFT spectra with parallel damping device under harmonic voltage disturbance

As illustrated in Fig. 11, after the direct-mounted damping device is connected in parallel, when background harmonic voltages are present in the grid and their frequencies coincide with the system’s series resonance points, neither uPCC nor ig exhibits harmonic oscillations, and waveform distortion remains minimal. The FFT spectra show that the total harmonic distortion (THD) of uPCC is 1.75%, and that of ig is 1.74%, both satisfying the harmonic limits for GCI system. In contrast, the id	 waveform contains abundant high-frequency harmonics and exhibits pronounced distortion. Its FFT analysis indicates a fundamental amplitude of 6.10 A and a THD of 12.40%, confirming that the high-frequency path provided by the damping device absorbs most grid harmonics. These results verify the effectiveness of the direct-mounted damping device in suppressing broadband harmonic oscillations in high DG penetration distribution networks.

  - Experimental verification

To further verify the general effectiveness of the direct-mounted damping device in suppressing broadband oscillations, an additional inverter was connected in parallel with the system shown in Fig. 2. Its control structure was identical to that of Inverter 2. The inverter control block diagram and detailed grid-connected parameters are provided in Appendix. The damping device parameters are listed in Table 6. The frequency-response curves of the system before and after the parallel connection of the direct-mounted damping device are plotted, as illustrated in Fig. 12.

Fig. 12 Frequency responses of the system with and without the damping device

As shown in Fig. 12, the multi-inverter grid-connected system exhibits three pairs of resonance peaks with a wide frequency span between them. After the direct-mounted damping device is connected in parallel, all three pairs of resonance peaks are significantly suppressed. The system’s characteristic roots, resonant frequencies, and damping ratios (ξ) before and after the connection of the direct-mounted damping device are calculated, and the results are presented in Table 8.

Tab.8 Eigenvalues, Resonance Frequencies, and Damping Coefficient ξ of the multi-inverter grid-connected system with / without the damping device

|  | characteristic root | Resonant frequency / Hz | ξ |
| --- | --- | --- | --- |
| Original system | λ1,2 = -4.68 ± j74.85 | 12 | 0.06 |
|  | λ3,4 = -92.63 ± j5529.1 | 832 | 0.018 |
|  | λ5,6 = -121.59± j13282 | 2114 | 0.009 |
|  | λ7,8= -121.59± j13282 | 3660 | 0.007 |
|  | λ9= -265350 | / | / |
| After connecting Direct-mounted Damping Device in Parallel | λ1 = -1.00 | / | / |
|  | λ2 = -481.95 | / | / |
|  | λ3,4 = -4.68 ± j74.85 | 12 | 0.06 |
|  | λ5,6 = -758.30 ± j5159.9 | 821 | 0.15 |
|  | λ7,8 = -1328.2 ± j13204 | 2101 | 0.10 |
|  | λ9,10 = -1781.4 ± j22759 | 3622 | 0.08 |
|  | λ11 = -267280 | / | / |

As shown in Table 8, the multi-inverter grid-connected system exhibits three pairs of series–parallel resonance points, with relatively small damping ratios (ξ) corresponding to the characteristic roots. After the direct-mounted damping device is connected in parallel, the ξ values of the characteristic roots increase significantly compared with those of the original system. These results are consistent with Fig. 12, confirming the effectiveness and general applicability of the proposed method in suppressing multimodal resonance peaks in high DG penetration distribution networks.

A model of the multi-inverter grid-connected system was developed on the RT-Lab hardware-in-the-loop (HIL) experimental platform, as illustrated in Fig. 13.

Fig.13  RT_Lab Hardware-in-the-Loop Real-Time Simulation Platform.

As indicated in Table 8, the multi-inverter grid-connected system exhibits three parallel resonance points at 832 Hz, 2114 Hz, and 3660 Hz. After the direct-mounted damping device is connected in parallel, these resonance frequencies shift to 821 Hz, 2101 Hz, and 3622 Hz. A harmonic current source was injected at node 3 of the system shown in Fig. 2, with its amplitude set to 1.5% of the rated grid current. Fig. 14, 15, and 16 respectively present the waveforms of uPCC and ig for the original system with and without harmonic disturbances, as well as for the system equipped with the direct-mounted damping device connected in parallel under harmonic current disturbances.

Fig. 14 uPCC and ig waveforms of the original system

Fig. 15 uPCC and ig waveforms under harmonic disturbances in the original system

Fig. 16 uPCC and ig waveforms with parallel damping under harmonic disturbances

As shown in Fig. 14, 15, and 16, when the original system operates under normal conditions, the uPCC and ig waveforms remain smooth with minimal harmonic content. However, once the system is subjected to harmonic disturbances, uPCC becomes severely distorted, and its harmonic components are significantly amplified, failing to meet the harmonic limits for GCI system. The ig waveform exhibits relatively moderate distortion but contains more harmonic components due to the coupling effect of uPCC. After the direct-mounted damping device is connected in parallel, neither uPCC nor ig shows harmonic oscillations under harmonic disturbances, and both waveforms exhibit only slight distortion. These results confirm the effectiveness of the direct-mounted damping device in suppressing multi-modal resonance peaks in the system, and demonstrates the general applicability of the proposed method for mitigating broadband harmonic oscillations in distribution network.

Conclusion

This paper proposes a method for suppressing multimodal broadband harmonic oscillations in high DG penetration distribution networks by deploying direct-mounted damping devices at key system nodes. Based on the topology and operating principles of the damping device, and considering the IEC-specified electromagnetic compatibility (EMC) levels for low-voltage distribution networks, a general procedure for device parameter design is developed. Simulation results verify the feasibility of the proposed method in mitigating broadband harmonic oscillations, while experimental results on a multi-inverter grid-connected system further demonstrate its generality and effectiveness. The main conclusions are summarized as follows:

1) A unified quantitative indicator suitable for broadband oscillation analysis was established. The even-order harmonic content in low-voltage distribution networks is relatively small; therefore, when the system’s resonant frequency is close to even-order harmonics, a damping coefficient of ξ ≥ 0.2 is sufficient to satisfy the harmonic limit requirements for GCI system.

2) The general procedure for designing the parameters of the direct-mounted damping device is developed using the modal analysis method and the PSO algorithm. The modal analysis method, as an analytical tool, enables fast and straightforward impedance modeling of the system, identification of resonance points, and evaluation of the excitability and observability of different nodes with respect to the resonant modes, thereby determining the optimal node for parallel damping device placement. The PSO algorithm, as an optimization technique, efficiently provides iterative parameter results of the damping device for a given objective function.

3) The effectiveness and general applicability of the direct-mounted damping devices in suppressing broadband harmonic oscillations in “dual-high” distribution networks have been verified. Designed to be connected in parallel at key nodes of the system, the devices significantly enhance the system’s damping coefficient, shift its resonant frequencies, and strengthen its capability to actively suppress harmonic oscillations without affecting its fundamental-frequency operating characteristics. Consequently, the proposed method effectively mitigates broadband oscillations induced by the integration of multiple inverters.

Appendix

The detailed control block diagram of the inverter in Fig. 2 is given in App.Fig. 1.

In App.Fig. 1, i1ref(s) and i2ref(s) denote the reference currents for the closed-loop control of the two inverters. kPWM represents the bridge gain; k1 and k2 are the active damping elements; G(s) is the proportional–integral controller. Its expressions is G(s) = kp + ki / s. Ts is the sampling period. The detailed parameters of the multi-inverter grid-connected system are listed in App.Tab. 1.

App.Fig. 1 Control block diagrams of the GCIs

App.Tab.1 Parameters of the multi-inverter grid-connected system

| Parameter | Values |  |  |
| --- | --- | --- | --- |
|  | Inverter 1 | Inverter 2 | Inverter 3 |
| L1 / mH | 1.65 | 0.6 | 1 |
| L2 / mH | 0.425 | 0.36 | 0.4 |
| C / μF | 56 | 7 | 15 |
| Vdc / V | 400 | 400 | 400 |
| iref / A | 25 | 30 | 30 |
| k1 | 1 | 0.0265 | 0.0285 |
| k2 | 1 | 0.0025 | 0045 |
| kPWM | 1 | 1 | 1 |
| G1(s) | 0.25 + 1 / s | 0.03 + 18 / s | 0.15 + 1 / s |
| Lg / mH | 1 |  |  |
| ug / V | 311 |  |  |
| f0 / Hz | 50 |  |  |
| Ts / s | 10-6 |  |  |

Section 3.1 presented several passive device topologies for broadband oscillation suppression. Their corresponding admittance expressions are given below.

Fig. 4a):

(A1)

Fig. 4b):

(A2)

Fig. 4c):

(A3)

Direct-mounted Damping Device:

(A4)

References

- F. Blaabjerg, R. Teodorescu, M. Liserre, and A. V. Timbus, “Overview of Control and Grid Synchronization for Distributed Power Generation Systems,” IEEE Trans. Ind. Electron., vol. 53, no. 5, pp. 1398-1409, Oct. 2006.

- X. Wang, and F. Blaabjerg, “Harmonic Stability in Power Electronic-Based Power Systems: Concept, Modeling, and Analysis,” IEEE Trans. Smart Grid, vol. 10, no. 3, pp. 2858-2870, May 2019.

- M. Zhao, X. Yuan, J. Hu, and Y. Yan, “Voltage Dynamics of Current Control Time-Scale in a VSC-Connected Weak Grid,” IEEE Trans. Power Syst., vol. 31, no. 4, pp. 2925-2937, Jul. 2016.

- C. Li, “Unstable Operation of Photovoltaic Inverter From Field Experiences,” IEEE Trans. Power Del., vol. 33, no. 2, pp. 1013-1015, Apr. 2018.

- F. Wang, J. L. Duarte, M. A. M. Hendrix, and P. F. Ribeiro, “Modeling and Analysis of Grid Harmonic Distortion Impact of Aggregated DG Inverters,” IEEE Trans. Power Electron., vol. 26, no. 3, pp. 786-797, Mar. 2011.

- Z. Chen, X. Huang, A. Luo, J. Yang, and L. Yang, “Wideband Harmonic Resonance Characteristics and Coordinated Damping Method for Distributed Generation Power Plants,” IEEE Trans. Ind. Electron., vol. 66, no. 10, pp. 7753-7764, Oct. 2019.

- S. Jian. “Impedance-based stability criterion for grid-connected inverters,” IEEE Trans. Power Electron., vol. 26, no. 11, pp. 3075-3078, Nov. 2011.

- L. Rong, L. Jianwen, L. Yonggang, and S. Wei, “Analysis of Harmonic Disturbance Response of Multi-Inverter Grid-Connected System Combining Characteristic Root and Modal Analysis Method,” Transactions of China Electrotechnical Society, vol. 39, no. 14, pp. 4519-4534, Jul. 2024.

- C. Xie, K. Li, J. Zou, and J. M. Guerrero, “Passivity-Based Stabilization of LCL-Type Grid-Connected Inverters via a General Admittance Model,” IEEE Trans. Power Electron., vol. 35, no. 6, pp. 6636-6648, Jun. 2020.

- Z. Xin, P. Mattavelli, W. Yao, Y. Yang, F. Blaabjerg, and P. C. Loh, “Mitigation of Grid-Current Distortion for LCL-Filtered Voltage-Source Inverter With Inverter-Current Feedback Control,” IEEE Trans. Power Electron., vol. 33, no. 7, pp. 6248-6261, Jul. 2018.

- M. Li, Y. Ren, H. Xiao, C. Niu, and M. Cheng, “An Equivalent Differential Method for Active Damping of LCL Type Grid-Connected Inverters With Grid-Side Inductor Voltage Feedback,” IEEE Trans. Power Electron., vol. 38, no. 6, pp. 7009-7021, Jun. 2023.

- Z. Zheng, L. Zhang, Y. Wang, Z. Lei, Y. Zou, and C. Wu, “Full Grid Voltage Feedforward for Critical Mode LCL-Type Single-Phase Grid-Tied Inverters With Physical Interpretations,” IEEE Trans. Power Electron., vol. 38, no. 4, pp. 5283-5295, Apr. 2023.

- L. Harnefors, X. Wang, A. G. Yepes, and F. Blaabjerg,,“Passivity-Based Stability Assessment of Grid-Connected VSCs-An Overview,” IEEE J. Emerg. Sel. Topics Power Electron., vol. 4, no. 1, pp. 116-125, Mar. 2016.

- X. Wang, F. Blaabjerg, P. C. Loh, “Passivity-Based stability analysis and damping injection for multiparalleled VSCs with LCL filters,” IEEE Transactions on Power Electron., vol. 32, no. 11, pp. 8922-8935, Nov. 2017.

- J. He, and Y. W. Li, “Generalized Closed-Loop Control Schemes with Embedded Virtual Impedances for Voltage Source Converters with LC or LCL Filters,” IEEE Trans. Power Electron., vol. 27, no. 4, pp. 1850-1861, Apr. 2012.

- D. Ding, J. Liu, W. Song, and P. Wheeler, “Extended Application of Improved D-D-Σ Current Control in Synchronous Inverter Cluster Considering N Times Equivalent Impedance,” IEEE Trans. Circuits Syst. I: Regular Papers, vol. 71, no. 3, pp. 1346-1357, Mar. 2024.

- J. Liu, X. Sun, Z. Chen, Y. Chi, W. Song, Q. Zhu, and P. Wheeler, “A Hybrid Multiresonances Suppression Method for Nonsynchronous LCL-Type Grid-Connected Inverter Clusters Under Weak Grid,” IEEE Trans. Power Electron., vol. 39, no. 5, pp.5386-5399, May 2024.

- P. Yi, G. Chunyi, D. Dongye, “Research on medium and high frequency oscillation suppression approach based on impedance tuning in flexible HVDC system,” Proceedings of the CSEE, vol. 42, no. 22, pp.8053-8062, Nov. 2022.

- H. Yanqi, L. Chongru, W. Yu, et al, “Research on the suppression strategy of high-frequency resonance for MMC-HVDC,” Proceedings of the CSEE, vol. 41, no. 11, pp. 3741-3750, Jun. 2021.

- S. H. E. A. Aleem, A. F. Zobaa, and M. M. A. Aziz, “Optimal C-Type passive filter based on minimization of the voltage harmonic distortion for nonlinear loads,” IEEE Transactions on Ind. Electron., vol. 59, no. 1, pp. 281-289, Jan. 2012.

- C. Ö. Gerçek, M. Ermis, A. Ertas, et al, “Design, implementation, and operation of a new C-Type 2nd harmonic filter for electric arc and ladle furnaces,” IEEE Transactions on Ind. Appl., vol. 47, no. 4, pp. 1545-1557, Jul./Aug. 2011.

- C. Zou, H. Rao, S. Xu, et al, “Analysis of Resonance Between a VSC-HVDC Converter and the AC Grid,” IEEE Transactions on Power Electron., vol. 33, no. 12, pp. 10157-10168, Dec. 2018.

- Z. Donghui, C. Xin, Y. Shuting, et al, “Analysis of high-frequency resonance and suppression strategy of photovoltaic power plant with static reactive power compensation device,” Proceedings of the CSEE, vol. 43, no. 24, pp. 9580-9593, Dec. 2023.

- Z. Qianjin, Z. Lin, L. Haixiao, et al, “Oscillation analysis and suppression of large-scale grid-connected photovoltaic system considering SVG equipment,” Proceedings of the CSEE, vol. 39, no. 9, pp. 2636-2643, May 2019.

- S. Wang, Y. Li, M. Zhang, Y. Peng, Y. Tian, G. Lin, and F. Chang, “Harmonic Resonance Suppression With Inductive Power Filtering Method: Case Study of Large-Scale Photovoltaic Plant in China,” IEEE Trans. Power Electron., vol. 38, no. 5, pp. 6444-6454, May 2023.

- W. Xu, Z. Huang, Y. Cui, and H. Wang, “Harmonic Resonance Mode Analysis,” IEEE Trans. Power Delivery, vol. 20, no. 2, pp. 1182-1190, Apr. 2005.

- L. Hong, W. Shu, J. Wang, and R. Mian, “Harmonic Resonance Investigation of a Multi-Inverter Grid-Connected System Using Resonance Modal Analysis,” IEEE Trans. Power Delivery, vol. 34, no. 1, pp. 63-72, Feb. 2019.

- Pereira M, Retzmann D, Lottes J, et al. SVC plus: an MMC STATCOM for network and grid access applications[C]//Proceedings of 2011 IEEE Trondheim PowerTech, Trondheim, Norway, 2011: 1-5.

- Electromagnetic Compatibility (EMC) - Environment - Compatibility levels for low-frequency conducted disturbances and signalling in public low-voltage power supply systems: DS/EN 61000-2-2: 2002/A2: 2019[S]. Danish Standards, 2019.

- Electromagnetic compatibility (EMC) – Part 3-15: Limits – Assessment of low frequency electromagnetic immunity and emission requirements for dispersed generation systems in LV network: IEC/TR 61000-3-15[S]. IEC, 2011.

- J. C. Das, “Practical passive filter designs,” in Power System Harmonic Passive Filter Designs, Hoboken, NJ, USA: Wiley, 2015.